## Description
SGC 420 and 421 Modbus descriptions
Row | Hyperlink index
11 | Modbus function codes
22 | Holding register
35 | Descrete_input_contact
Back to index | Modbus function codes
| Function code | Description
| 03 | Read a single or multiple 16-bit registers from the server device location.
| 02 | Read a single or multiple 16-bit registers from the server device location.
| 16 | Write a value to a single or multiple 16-bit registers to the server device.
Back to index | Holding register
| Function code | Effect
| 03 | Read
| 16 | Write
| Function group | Description
| AC measurement | Read the operating value of the associated AC measurement.
| Energy counter | Read the counter value.
| Engine measurement | Read the operating value of the associated engine measurement.
| Running hours | Read the running hours value
| Alarm status | Read the alarm status
| Input and output status | Read the state of a digital input or output on the controller. The controller returns 0 (false) when the digital input/output is inactive. The controller returns 1 (true) when the digital input/output is active.
| DG status | Read the status of the genset.
| DG mode change | Write: The controller changes the state of the genset if a valid value is entered.
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Digital input | Read the state of a digital input on the controller. The controller returns 0 (false) when the digital input is inactive. The controller returns 1 (true) when the digital input is active.

## Holding register (03;16)
Holding register (03;16)
Function group | Modbus address | Modbus function code | Parameter | Data type | Scaling | Unit
Protocol revision | 0 | 03 | Protocol revision | Unsigned | 0.1 | -
AC measurement | 1 | 03 | Generator L1-n voltage | Unsigned | 0.1 | V
AC measurement | 2 | 03 | Generator L2-n voltage | Unsigned | 0.1 | V
AC measurement | 3 | 03 | Generator L3-n voltage | Unsigned | 0.1 | V
AC measurement | 4 | 03 | Generator L1-L2 voltage | Unsigned | 0.1 | V
AC measurement | 5 | 03 | Generator L2-L3 voltage | Unsigned | 0.1 | V
AC measurement | 6 | 03 | Generator L3-L1 voltage | Unsigned | 0.1 | V
AC measurement | 7 | 03 | Generator R frequency | Unsigned | 0.1 | Hz
AC measurement | 8 | 03 | Generator Y frequency | Unsigned | 0.1 | Hz
AC measurement | 9 | 03 | Generator B frequency | Unsigned | 0.01 | Hz
AC measurement | 10 | 03 | Generator power factor L1 | Unsigned | 0.01 | -
AC measurement | 11 | 03 | Generator power factor L2 | Unsigned | 0.01 | -
AC measurement | 12 | 03 | Generator power factor L3 | Unsigned | 0.01 | -
AC measurement | 13 | 03 | Generator average power factor | Unsigned | 0.1 | -
AC measurement | 14 | 03 | Mains L1-n voltage | Unsigned | 0.1 | V
AC measurement | 15 | 03 | Mains L2-n voltage | Unsigned | 0.1 | V
AC measurement | 16 | 03 | Mains L3-n voltage | Unsigned | 0.1 | V
AC measurement | 17 | 03 | Mains L1-L2 voltage | Unsigned | 0.1 | V
AC measurement | 18 | 03 | Mains L2-L3 voltage | Unsigned | 0.1 | V
AC measurement | 19 | 03 | Mains L3-L1 voltage | Unsigned | 0.1 | V
AC measurement | 20 | 03 | Mains R frequency | Unsigned | 0.1 | Hz
AC measurement | 21 | 03 | Mains Y frequency | Unsigned | 0.1 | Hz
AC measurement | 22 | 03 | Mains B frequency | Unsigned | 0.1 | Hz
AC measurement | 23 | 03 | Load L1 current | Unsigned | 0.1 | A
AC measurement | 24 | 03 | Load L2 current | Unsigned | 0.1 | A
AC measurement | 25 | 03 | Load L3 current | Unsigned | 0.1 | A
AC measurement | 26 | 03 | Load L1 watts | Unsigned | 0.1 | KW
AC measurement | 27 | 03 | Load L2 watts | Unsigned | 0.1 | KW
AC measurement | 28 | 03 | Load L3 watts | Unsigned | 0.1 | KW
AC measurement | 29 | 03 | Load total watts | Unsigned | 1 | KW
AC measurement | 30 | 03 | Percentage Load | Unsigned | 0.1 | KW
AC measurement | 31 | 03 | Load L1 va | Unsigned | 0.1 | KVA
AC measurement | 32 | 03 | Load L2 va | Unsigned | 0.1 | KVA
AC measurement | 33 | 03 | Load L3 va | Unsigned | 0.1 | KVA
AC measurement | 34 | 03 | Load total va | Unsigned | 0.1 | KVA
AC measurement | 35 | 03 | Load L1 var | Unsigned | 0.1 | KVAR
AC measurement | 36 | 03 | Load L2 var | Unsigned | 0.1 | KVAR
AC measurement | 37 | 03 | Load L3 var | Unsigned | 0.1 | KVAR
AC measurement | 38 | 03 | Load total var | Unsigned | 0.1 | KVAR
Energy counter | 39-40 | 03 | Generator cumulative energy | Unsigned | 0.1 | KWh
Energy counter | 41-42 | 03 | Generator cumulative apparent energy | Unsigned | 0.1 | KVAh
Energy counter | 43-44 | 03 | Generator cumulative reactive energy | Unsigned | 0.1 | KVARh
Energy counter | 45-46 | 03 | Mains cumulative energy | Unsigned | 0.1 | KWh
Energy counter | 47-48 | 03 | Mains cumulative apparent energy | Unsigned | 0.1 | KVAh
Energy counter | 49-50 | 03 | Mains cumulative reactive energy | Unsigned | 0.1 | KVARh
Engine measurement | 51 | 03 | Oil pressure & LOP From ECU | Unsigned | 0.1 | Bar
Engine measurement | 52 | 03 | Coolant temperature & CLNT Temp from ECU | Unsigned | 1 | Deg C
Engine measurement | 53 | 03 | Fuel level | Unsigned | 0.1 | %
Engine measurement | 54 | 03 | Fuel Level in lit | Unsigned | 0.1 | lit
Engine measurement | 55 | 03 | Charge alternator voltage | Unsigned | 0.1 | V
Engine measurement | 56 | 03 | Battery voltage & Battery Vtg from ECU | Unsigned | 1 | V
Engine measurement | 57 | 03 | Engine speed & Speed from ECU | Unsigned | 1 | RPM
Engine measurement | 58 | 03 | No of starts | Unsigned | 1 | -
Engine measurement | 59 | 03 | No of trips | Unsigned | - | -
Running hours | 60 | 03 | Eng run hrs & Run hrs from ECU (more than 65535 from ECU) |  | 1 | -
Running hours | 61 | 03 | Eng run hrs & Run hrs from ECU | Unsigned | 1 | Hrs
Running hours | 62 | 03 | Eng run min & Run hrs from ECU | Unsigned | 1 | Min
Running hours | 63 | 03 | Mains run hrs | Unsigned | 1 | Hrs
Auxiliary input | 64 | 03 | Mains run min | Unsigned | 0.1 | Min
Auxiliary input | 65 | 03 | Auxiliary Input S1 value | signed | 0.1 | -
Auxiliary input | 66 | 03 | Auxiliary Input S2 value | signed | 0.1 | -
Auxiliary input | 67 | 03 | Auxiliary Input S3 value | signed | 0.1 | -
Auxiliary input | 68 | 03 | Auxiliary Input S4 value | signed | 0.1 | -
Site battery | 69 | 03 | Site Battery Voltage | Unsigned | 1 | -
Site battery | 70 | 03 | Site Battery Run time hrs | Unsigned | 1 | -
Site battery | 71 | 03 | Site Battery Run time mins | Unsigned | - | -
Function group | Modbus address | Modbus function code | Parameter | Data type | Scaling | Unit
Alarm Status for Alarm 1 | 72 | 03 | Low oil pressure | 13/16-16/16 | - | -
Alarm Status for Alarm 1 | 72 | 03 | High coolant temperature | 9/16-12/16 | - | -
Alarm Status for Alarm 1 | 72 | 03 | Low fuel level | 5/16-8/16 | - | -
Alarm Status for Alarm 1 | 72 | 03 | Water level switch | 1/16-4/16 | - | -
Alarm Status for Alarm 2 | 73 | 03 | Under speed | 13/16-16/16 | - | -
Alarm Status for Alarm 2 | 73 | 03 | Over speed | 9/16-12/16 | - | -
Alarm Status for Alarm 2 | 73 | 03 | Fail to start | 5/16-8/16 | - | -
Alarm Status for Alarm 2 | 73 | 03 | Fail to stop | 1/16-4/16 | - | -
Alarm Status for Alarm 3 | 74 | 03 | Shelter temperature open circuit | 13/16-16/16 | - | -
Alarm Status for Alarm 3 | 74 | 03 | High shelter temp | 9/16-12/16 | - | -
Alarm Status for Alarm 3 | 74 | 03 | Generator low frequency | 5/16-8/16 | - | -
Alarm Status for Alarm 3 | 74 | 03 | Generator high Frequency | 1/16-4/16 | - | -
Alarm Status for Alarm 4 | 75 | 03 | Generator high current | 13/16-16/16 | - | -
Alarm Status for Alarm 4 | 75 | 03 | Generator overload | 9/16-12/16 | - | -
Alarm Status for Alarm 4 | 75 | 03 | Unbalanced load | 5/16-8/16 | - | -
Alarm Status for Alarm 4 | 75 | 03 | Emergency stop | 1/16-4/16 | - | -
Alarm Status for Alarm 5 | 76 | 03 | Charge alternator failure | 13/16-16/16 | - | -
Alarm Status for Alarm 5 | 76 | 03 | Oil filter maintenance / filter maintenance | 9/16-12/16 | - | -
Alarm Status for Alarm 5 | 76 | 03 | MIL lamp (Automation) | 5/16-8/16 | Reserved | -
Alarm Status for Alarm 5 | 76 | 03 | Red lamp (Automation) | 1/16-4/16 | Reserved | -
Alarm Status for Alarm 6 | 77 | 03 | Battery low voltage | 13/16-16/16 | - | -
Alarm Status for Alarm 6 | 77 | 03 | Battery high voltage | 9/16-12/16 | - | -
Alarm Status for Alarm 6 | 77 | 03 | Engine Temperature Circuit open | 5/16-8/16 | - | -
Alarm Status for Alarm 6 | 77 | 03 | Reverse Power Detected | 1/16-4/16 | - | -
Alarm Status for Alarm 7 | 78 | 03 | Fuel theft | 13/16-16/16 | - | -
Alarm Status for Alarm 7 | 78 | 03 | Magnetic pick up fault | 9/16-12/16 | - | -
Alarm Status for Alarm 7 | 78 | 03 | Oil pressure circuit open | 5/16-8/16 | - | -
Alarm Status for Alarm 7 | 78 | 03 | Reserved | 1/16-4/16 | Reserved | -
Alarm Status for Alarm 8 | 79 | 03 | Auxiliary input A | 13/16-16/16 | - | -
Alarm Status for Alarm 8 | 79 | 03 | Auxiliary input B | 9/16-12/16 | - | -
Alarm Status for Alarm 8 | 79 | 03 | Auxiliary input C | 5/16-8/16 | - | -
Alarm Status for Alarm 8 | 79 | 03 | Auxiliary input D | 1/16-4/16 | - | -
Alarm Status for Alarm 9 | 80 | 03 | Auxiliary input E | 13/16-16/16 | - | -
Alarm Status for Alarm 9 | 80 | 03 | Auxiliary input F | 9/16-12/16 | - | -
Alarm Status for Alarm 9 | 80 | 03 | Auxiliary input G | 5/16-8/16 | - | -
Alarm Status for Alarm 9 | 80 | 03 | Auxiliary input H | 1/16-4/16 | - | -
Alarm Status for Alarm 10 | 81 | 03 | Auxiliary input I | 13/16-16/16 | - | -
Alarm Status for Alarm 10 | 81 | 03 | Auxiliary input J | 9/16-12/16 | - | -
Alarm Status for Alarm 10 | 81 | 03 | Auxiliary input K | 5/16-8/16 | - | -
Alarm Status for Alarm 10 | 81 | 03 | Auxiliary input L | 1/16-4/16 | - | -
Alarm Status for Alarm 11 | 82 | 03 | Auxiliary input M | 13/16-16/16 | - | -
Alarm Status for Alarm 11 | 82 | 03 | Auxiliary input N | 9/16-12/16 | - | -
Alarm Status for Alarm 11 | 82 | 03 | Auxiliary input O | 5/16-8/16 | - | -
Alarm Status for Alarm 11 | 82 | 03 | Auxiliary input P | 1/16-4/16 | - | -
Alarm Status for Alarm 12 | 83 | 03 | Gen L1 phase low volt | 13/16-16/16 | - | -
Alarm Status for Alarm 12 | 83 | 03 | Gen L1 phase high volt | 9/16-12/16 | - | -
Alarm Status for Alarm 12 | 83 | 03 | Gen L2 phase low volt | 5/16-8/16 | - | -
Alarm Status for Alarm 12 | 83 | 03 | Gen L2 phase high volt | 1/16-4/16 | - | -
Alarm Status for Alarm 13 | 84 | 03 | Gen L3 phase low volt | 13/16-16/16 | - | -
Alarm Status for Alarm 13 | 84 | 03 | Gen L3 phase high volt | 9/16-12/16 | - | -
Alarm Status for Alarm 13 | 84 | 03 | Dg phase rotation | 5/16-8/16 | - | -
Alarm Status for Alarm 13 | 84 | 03 | Mains phase rotation | 1/16-4/16 | - | -
Alarm Status for Alarm 14 | 85 | 03 | Low Load | 13/16-16/16 | - | -
Alarm Status for Alarm 14 | 85 | 03 | V belt broken | 9/16-12/16 | - | -
Alarm Status for Alarm 14 | 85 | 03 | Open Ckt fuel level | 5/16-8/16 | - | -
Alarm Status for Alarm 14 | 85 | 03 | High oil pressure detected | 1/16-4/16 | - | -
Alarm Status for Alarm 15 | 86 | 03 | Auxiliary Input S4 | 13/16-16/16 | - | -
Alarm Status for Alarm 15 | 86 | 03 | Auxiliary Input S3 | 9/16-12/16 | - | -
Alarm Status for Alarm 15 | 86 | 03 | Auxiliary Input S2 | 5/16-8/16 | - | -
Alarm Status for Alarm 15 | 86 | 03 | Auxiliary Input S1 | 1/16-4/16 | - | -
Alarm Status for Alarm 16 | 87 | 03 | Auxiliary S4 open Ckt alarm | 13/16-16/16 | - | -
Alarm Status for Alarm 16 | 87 | 03 | Auxiliary S3 open Ckt alarm | 9/16-12/16 | - | -
Alarm Status for Alarm 16 | 87 | 03 | Auxiliary S2 open Ckt alarm | 5/16-8/16 | - | -
Alarm Status for Alarm 16 | 87 | 03 | Auxiliary S1 open Ckt alarm | 1/16-4/16 | - | -
Alarm Status for Alarm 17 | 88 | 03 | Auxiliary S4 Short to battery | 13/16-16/16 | - | -
Alarm Status for Alarm 17 | 88 | 03 | Auxiliary S3 Short to battery | 9/16-12/16 | - | -
Alarm Status for Alarm 17 | 88 | 03 | AFT Activation Timeout | 5/16-8/16 | - | -
Alarm Status for Alarm 17 | 88 | 03 | Ash Load Maintenance | 1/16-4/16 | - | -
Interpretation of alarm status results
Value of Register | Interpretation
0 | Alarm disabled
1 | Alarm not active
2 | Warning alarm active
3 | Shutdown alarm active
4 | Electrical trip alarm active
5 | Notification
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
Input diagnostics | 89 | 03 | Digital input A | 16/16 | - | -
Input diagnostics |  | 03 | Digital input B | 15/16 | - | -
Input diagnostics |  | 03 | Digital input C | 14/16 | - | -
Input diagnostics |  | 03 | Digital input D | 13/16 | - | -
Input diagnostics |  | 03 | Digital input E | 12-16 | - | -
Input diagnostics |  | 03 | Digital input F | 11-16 | - | -
Input diagnostics |  | 03 | Digital input G | 10-16 | - | -
Input diagnostics |  | 03 | Digital input H | 9-16 | - | -
Input diagnostics |  | 03 | Digital input I | 8-16 | - | -
Input diagnostics |  | 03 | Digital input J | 7-16 | - | -
Input diagnostics |  | 03 | Digital input K | 6-16 | - | -
Input diagnostics |  | 03 | Digital input L | 5-16 | - | -
Input diagnostics |  | 03 | Digital input M | 4-16 | - | -
Input diagnostics |  | 03 | Digital input N | 3-16 | - | -
Input diagnostics |  | 03 | Digital input O | 2-16 | - | -
Input diagnostics |  | 03 | Digital input P | 1-16 | - | -
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
Output diagnostics | 90 | 03 | Digital output A | 16/16 | - | -
Output diagnostics |  | 03 | Digital output B | 15/16 | - | -
Output diagnostics |  | 03 | Digital output C | 14/16 | - | -
Output diagnostics |  | 03 | Digital output D | 13/16 | - | -
Output diagnostics |  | 03 | Digital output E | 12-16 | - | -
Output diagnostics |  | 03 | Digital output F | 11-16 | - | -
Output diagnostics |  | 03 | Digital output G | 10-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 9-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 8-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 7-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 6-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 5-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 4-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 3-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 2-16 | - | -
Output diagnostics |  | 03 | Unimplemented | 1-16 | - | -
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
DG status | 91 | 03 | SGC Mode | 16/16 | - | Config (1)/Running or Not running (0)
DG status | 91 | 03 | Mains healthy / unhealthy | 15/16 | - | True (1) / False(0)
DG status | 91 | 03 | DG operation mode | 12-14/16 | - | Scheduler-110 Auto-101 Manual-100
DG status | 91 | 03 | Load on Mains | 11-16 | - | True (1) / False(0)
DG status | 91 | 03 | Load on DG | 10-16 | - | True (1) / False(0)
DG status | 91 | 03 | Current DG status | 9-16 | - | Running / stopped
DG status | 91 | 03 | DG stopped normally | 8-16 | - | True (1) / False(0)
DG status | 91 | 03 | DG stopped with fault | 7-16 | - | True (1) / False(0)
DG status | 91 | 03 | DG fail to start | 6-16 | - | True (1) / False(0)
DG status | 91 | 03 | Gen available | 5-16 | - | True (1) / False(0)
DG status | 91 | 03 | Common shut down | 4-16 | - | True (1) / False(0)
DG status | 91 | 03 | Common electric trip | 3-16 | - | True (1) / False(0)
DG status | 91 | 03 | Common warning | 2-16 | - | True (1) / False(0)
DG status | 91 | 03 | Common notification | 1-16 | - | True (1) / False(0)
DG status | 92-95 | 03 | Current time stamp | - | - | -
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
Read register 2: AC measurement | 501 | 03 | Generator L1-L2 voltage | 4 | 0.1 | V
Read register 2: AC measurement | 502 | 03 | Generator L2-L3 voltage | 5 | 0.1 | V
Read register 2: AC measurement | 503 | 03 | Generator L3-L1 voltage | 6 | 0.1 | V
Read register 2: AC measurement | 504 | 03 | Generator L1-n voltage | 1 | 0.1 | V
Read register 2: AC measurement | 505 | 03 | Generator L2-n voltage | 2 | 0.1 | V
Read register 2: AC measurement | 506 | 03 | Generator L3-n voltage | 3 | 0.1 | V
Read register 2: AC measurement | 507 | 03 | Generator R frequency | 7 | 0.1 | Hz
Read register 2: AC measurement | 508 | 03 | Generator Y frequency | 8 | 0.1 | Hz
Read register 2: AC measurement | 509 | 03 | Generator B frequency | 9 | 0.1 | Hz
Read register 2: AC measurement | 513 | 03 | Load L1 current | 23 | 0.1 | A
Read register 2: AC measurement | 514 | 03 | Load L2 current | 24 | 0.1 | A
Read register 2: AC measurement | 515 | 03 | Load L3 current | 25 | 0.1 | A
Read register 2: AC measurement | 516 | 03 | Load L1 watts | 26 | 0.1 | kW
Read register 2: AC measurement | 517 | 03 | Load L2 watts | 27 | 0.1 | kW
Read register 2: AC measurement | 518 | 03 | Load L3 watts | 28 | 0.1 | kW
Read register 2: AC measurement | 519 | 03 | Load total watts | 29 | 0.1 | kW
Read register 2: Engine measurement | 555-556 | 03 | Eng run hrs (more than 65535 from ECU) Eng run hrs | 60-61 | 1 | Hrs
Read register 2: Engine measurement | 567 | 03 | Battery voltage | 56 | 0.1 | V
Read register 2: Engine measurement | 583 | 03 | Fuel level | 53 | 1 | -
Read register 2: Engine measurement | 584 | 03 | Oil pressure | 51 | 0.1 | -
Read register 2: Engine measurement | 585 | 03 | Coolant temperature | 52 | 0.1 | -
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
Read register 3: Alarm status | 1000 | 03 | Over Current Alarms status | 4th bit | 0.1 | Alarm present : 1 Alarm absent : 0
Read register 3: Alarm status | 1001 | 03 | Under Frequency Warning Alarm Status | 4th bit | 0.1 | Alarm present : 1 Alarm absent : 0
Read register 3: Alarm status | 1007 | 03 | Dig In E & G Alarm status | DIG_IN_E: 4th bit DIG_IN_G : 6th bit | 0.1 | Alarm present: 1 Alarm absent: 0
Read register 3: Alarm status | 1013 | 03 | Fail To Start Alarm Status | 16th bit | 0.1 | Alarm present : 1 Alarm absent : 0
Read register 3: Alarm status | 1014 | 03 | Fail To Stop Alarm Status | 1st Bit | 0.1 | Alarm present : 1 Alarm absent : 0
Read register 3: Mode information | 1019 | 03 | Operating Mode info (Manual /Auto) | Manual mode: 2nd Bit Auto Mode : 4th Bit | 0.1 | mode slected : 1 mode not selected: 0
Function group | Register Address | Modbus function code | Parameter | Data type | Scaling | Unit
DG mode change | 0 | 16 | DG mode change command | Unsigned | - | SGC STOP KEY (0x01), Decimal value:01 SGC START KEY (0x02), Decimal value:02 SGC AUTO KEY (0x04), Decimal value:04 SGC ACK KEY (0x40), Decimal value:64 Only one value at a time

## Discrete input contact (02)
Function group | Register Address | Modbus function code | Parameter | Data type | Unit
Digital input | 22500 | 02 | Digital input A | 16/16 | Enable:1 Disable:0
Digital input | 22501 | 02 | Digital input B | 15/16 | Enable:1 Disable:0
Digital input | 22502 | 02 | Digital input C | 14/16 | Enable:1 Disable:0
Digital input | 22503 | 02 | Digital input D | 13/16 | Enable:1 Disable:0
Digital input | 22504 | 02 | Digital input E | 12-16 | Enable:1 Disable:0
Digital input | 22505 | 02 | Digital input F | 11-16 | Enable:1 Disable:0
Digital input | 22506 | 02 | Digital input G | 10-16 | Enable:1 Disable:0
Digital input | 22507 | 02 | Digital input H | 9-16 | Enable:1 Disable:0
Digital input | 22516 | 02 | Digital input I | 4-16 | Enable:1 Disable:0
Digital input | 22517 | 02 | Digital input P | 5-16 | Enable:1 Disable:0
Digital input | 22518 | 02 | Digital input O | 6-16 | Enable:1 Disable:0
Digital input | 22581 | 02 | Digital input N | 5-16 | Enable:1 Disable:0
Digital input | 22582 | 02 | Digital input M | 6/81 | Enable:1 Disable:0
Digital input | 22591 | 02 | Digital input L | 15/16 | Enable:1 Disable:0
Digital input | 22592 | 02 | Digital input K | 16/16 | Enable:1 Disable:0
Digital input | 22593 | 02 | Digital input J | 1-16 | Enable:1 Disable:0