## Descriptions
ASC-4 Modbus descriptions
Software version
The information contained in these tables (Revision K) is applicable to software version 4.26.0 of the ASC-4.
More information
See the ASC-4 Modbus server User manual.
Row | Hyperlink index
16 | Modbus function codes
27 | Discrete output coil
35 | Discrete input contact
43 | Output holding register
67 | Input register
Back to index | Modbus function codes
| Function code | Description
| 01 | Read a single or multiple discrete output coils.
| 02 | Read a single or multiple discrete input contacts.
| 03 | Read a single or multiple output holding registers.
| 04 | Read a single or multiple input registers.
| 05 | Write a value to a single discrete output coil.
| 06 | Write a value to a single output holding register.
| 15 | Write a value to multiple consecutive discrete output coils.
| 16 | Write a value to multiple consecutive output holding registers.
Back to index | Discrete output coil
| Function code | Effect
| 01 | Read
| 05 or 15 | Write
| Function group | Description
| Command flag | Activate a command in the controller. Read: The controller always returns 0 (false). Write: The controller executes the command if you write 1 (true).
Back to index | Discrete input contact
| Function code | Effect
| 02 | Read
| Function group | Description
| Digital input | Read the state of a digital input on the controller. The controller returns 0 (false) when the digital input is inactive. The controller returns 1 (true) when the digital input is active.
| Digital output | Read the state of a digital output on the controller. The controller returns 0 (false) when the digital output is inactive. The controller returns 1 (true) when the digital output is active.
Back to index | Output holding register
| Function code | Effect
| 03 | Read
| 06 or 16 | Write
| Function group | Description
| Control command | Activate a command in the controller. Read: The controller always returns 0 (false) from the bits. Write: The controller executes the command if you write 1 (true) to the address bit.
| Control time command | Read and write the time and date values of the controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
| Read area 1 (ASC to PLC/external system) | Part of the DEIF Open protocol. The ASC puts data here for a PLC or external system to read.
| Read area 2 (ASC to PLC/external system) | Part of the DEIF Open protocol. The ASC puts data here for a PLC or external system to read.
| Read/Write (Battery) | Read and write for a battery controller. Read: The controller returns the value of the associated function. Write: The controller changes the value of the associated function if a valid value is entered.
| SunSpec 'C001': Common model | SunSpec server support: The Common model defines the start of a SunSpec map with unique ID.
| SunSpec 'E302': Irradiation model | SunSpec server support.
| SunSpec 'E303': Back of module temperature model | SunSpec server support.
| SunSpec 'E307': Base meteorological model | SunSpec server support.
| SunSpec 'End model' | SunSpec server support.
| SunSpec 'I103': Inverter model | SunSpec server support. For more information, see the Modbus client and Modbus server document.
| SunSpec 'I120': Name plate model | SunSpec server support.
| SunSpec 'I121': Inverter controls basic settings model | SunSpec server support.
| SunSpec 'I122': Inverter controls extended measurements and status model | SunSpec server support.
| SunSpec 'I123': Immediate control model | SunSpec server support. For more information, see the Modbus client and Modbus server document.
| Weather area | Weather data.
| Write area 1 (PLC/external system to ASC) | Part of the DEIF Open protocol. A PLC or external system writes data here for the ASC to use.
Back to index | Input register
| Function code | Effect
| 04 | Read
| Function group | Description
| AC alarm | Read one bit to see whether the AC alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| AC measurement | Read the operating value of the associated AC measurement.
| Alarm | Read one bit to see whether the alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| APPL version | Read the controller application version.
| Control command state | Read the state of all the bits in the control command address.
| Counter | Read the counter value.
| DC measurement | Read the operating value of the associated measurement.
| Forecast area 1 | Read the forecast data.
| Forecast area 2 | Read the forecast configuration.
| M-Logic state | Read one bit to see whether the M-Logic virtual event or flip-flop is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Modes | Read one bit to see whether the mode is activated. The controller returns 0 (false) when the mode is not activated. The controller returns 1 (true) when the mode is activated.
| Modbus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 499 are available for configurable Modbus. For more information, see the Modbus server document.
| Plant logic state | Read one bit to see whether the state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| PM AC measurement | Read the operating value of the associated Power Management measurements and settings.
| PM alarm | Read one bit to see whether the Power Management alarm is activated. The controller returns 0 (false) when the alarm is not activated. The controller returns 1 (true) when the alarm is activated.
| PM Plant logic state | Read one bit to see whether the Power Management state is activated. The controller returns 0 (false) when the state is not activated. The controller returns 1 (true) when the state is activated.
| Power meter area 1 | Read the operating value of the associated power meters.
| Profibus configurable area | Read the value of the function assigned to the address using the Modbus configurator. Additional information about the assigned address should be completed by the user. Modbus addresses 0 to 62 are available for configurable Profibus. For more information, see the Modbus server document.
| PV monitoring area | The ASC Modbus client can poll key data from the inverter(s) and place it in the designated Modbus server area for a monitoring system to read. PV monitoring can be used with unicast and broadcast topologies. The number of nodes determines the number of inverters the ASC should poll data from. A maximum of 42 nodes can be monitored. The ASC expects that the ModbusIDs of the inverters are consecutive in order starting from the selected ModbusID and forward. 70 registers are reserved for each inverter. The Modbus addresses are only for the first inverter. Registers for the following inverters are consecutive.
| Relay state | Read one bit to see whether the relay is activated. The controller returns 0 (false) when the relay is not activated. The controller returns 1 (true) when the relay is activated.

## Discrete output coil (01;05;15)
Discrete output coil (01;05;15)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | SOLAR | BATT
Command flag | 0 | 1 | 01; 05; 15 | Semi start | X | X
Command flag | 1 | 2 | 01; 05; 15 | ESB close |  | X
Command flag | 1 | 2 | 01; 05; 15 | PVB close | X
Command flag | 2 | 3 | 01; 05; 15 | ESB open |  | X
Command flag | 2 | 3 | 01; 05; 15 | PVB open | X
Command flag | 3 | 4 | 01; 05; 15 | Semi stop | X | X
Command flag | 9 | 10 | 01; 05; 15 | Alarm ack. | X | X
Command flag | 16 | 17 | 01; 05; 15 | Island | X | X
Command flag | 18 | 19 | 01; 05; 15 | Peak shaving | X | X
Command flag | 19 | 20 | 01; 05; 15 | Fixed power | X | X
Command flag | 20 | 21 | 01; 05; 15 | Mains power export (MPE) | X | X
Command flag | 26 | 27 | 01; 05; 15 | Auto start | X | X
Command flag | 27 | 28 | 01; 05; 15 | Auto stop | X | X
Command flag | 36 | 37 | 01; 05; 15 | Capacitive PF | X | X
Command flag | 38 | 39 | 01; 05; 15 | 1st priority | X | X
Command flag | 40 | 41 | 01; 05; 15 | Application 1 | X | X
Command flag | 41 | 42 | 01; 05; 15 | Application 2 | X | X
Command flag | 42 | 43 | 01; 05; 15 | Application 3 | X | X
Command flag | 43 | 44 | 01; 05; 15 | Application 4 | X | X
Command flag | 46 | 47 | 01; 05; 15 | Synchronise clock to 4:00 a.m. | X | X
Command flag | 48 | 49 | 01; 05; 15 | Virtual event 1 | X | X
Command flag | 49 | 50 | 01; 05; 15 | Virtual event 2 | X | X
Command flag | 50 | 51 | 01; 05; 15 | Virtual event 3 | X | X
Command flag | 51 | 52 | 01; 05; 15 | Virtual event 4 | X | X
Command flag | 52 | 53 | 01; 05; 15 | Virtual event 5 | X | X
Command flag | 53 | 54 | 01; 05; 15 | Virtual event 6 | X | X
Command flag | 54 | 55 | 01; 05; 15 | Virtual event 7 | X | X
Command flag | 55 | 56 | 01; 05; 15 | Virtual event 8 | X | X
Command flag | 56 | 57 | 01; 05; 15 | Virtual event 9 | X | X
Command flag | 57 | 58 | 01; 05; 15 | Virtual event 10 | X | X
Command flag | 58 | 59 | 01; 05; 15 | Virtual event 11 | X | X
Command flag | 59 | 60 | 01; 05; 15 | Virtual event 12 | X | X
Command flag | 60 | 61 | 01; 05; 15 | Virtual event 13 | X | X
Command flag | 61 | 62 | 01; 05; 15 | Virtual event 14 | X | X
Command flag | 62 | 63 | 01; 05; 15 | Virtual event 15 | X | X
Command flag | 63 | 64 | 01; 05; 15 | Virtual event 16 | X | X
Command flag | 64 | 65 | 01; 05; 15 | Virtual event 17 | X | X
Command flag | 65 | 66 | 01; 05; 15 | Virtual event 18 | X | X
Command flag | 66 | 67 | 01; 05; 15 | Virtual event 19 | X | X
Command flag | 67 | 68 | 01; 05; 15 | Virtual event 20 | X | X
Command flag | 68 | 69 | 01; 05; 15 | Virtual event 21 | X | X
Command flag | 69 | 70 | 01; 05; 15 | Virtual event 22 | X | X
Command flag | 70 | 71 | 01; 05; 15 | Virtual event 23 | X | X
Command flag | 71 | 72 | 01; 05; 15 | Virtual event 24 | X | X
Command flag | 72 | 73 | 01; 05; 15 | Virtual event 25 | X | X
Command flag | 73 | 74 | 01; 05; 15 | Virtual event 26 | X | X
Command flag | 74 | 75 | 01; 05; 15 | Virtual event 27 | X | X
Command flag | 75 | 76 | 01; 05; 15 | Virtual event 28 | X | X
Command flag | 76 | 77 | 01; 05; 15 | Virtual event 29 | X | X
Command flag | 77 | 78 | 01; 05; 15 | Virtual event 30 | X | X
Command flag | 78 | 79 | 01; 05; 15 | Virtual event 31 | X | X
Command flag | 79 | 80 | 01; 05; 15 | Virtual event 32 | X | X
Command flag | 121 | 122 | 01; 05; 15 | Clear log | X | X
Command flag | 122 | 123 | 01; 05; 15 | Clear Parameter edits | X | X
Command flag | 135 | 136 | 01; 05; 15 | Reset horn | X | X
Command flag | 136 | 137 | 01; 05; 15 | Activate manual memory backup | X | X
Command flag | 137 | 138 | 01; 05; 15 | Set flipflop 01 | X | X
Command flag | 138 | 139 | 01; 05; 15 | Set flipflop 02 | X | X
Command flag | 139 | 140 | 01; 05; 15 | Set flipflop 03 | X | X
Command flag | 140 | 141 | 01; 05; 15 | Set flipflop 04 | X | X
Command flag | 141 | 142 | 01; 05; 15 | Set flipflop 05 | X | X
Command flag | 142 | 143 | 01; 05; 15 | Set flipflop 06 | X | X
Command flag | 143 | 144 | 01; 05; 15 | Set flipflop 07 | X | X
Command flag | 144 | 145 | 01; 05; 15 | Set flipflop 08 | X | X
Command flag | 145 | 146 | 01; 05; 15 | Set flipflop 09 | X | X
Command flag | 146 | 147 | 01; 05; 15 | Set flipflop 10 | X | X
Command flag | 147 | 148 | 01; 05; 15 | Set flipflop 11 | X | X
Command flag | 148 | 149 | 01; 05; 15 | Set flipflop 12 | X | X
Command flag | 149 | 150 | 01; 05; 15 | Set flipflop 13 | X | X
Command flag | 150 | 151 | 01; 05; 15 | Set flipflop 14 | X | X
Command flag | 151 | 152 | 01; 05; 15 | Set flipflop 15 | X | X
Command flag | 152 | 153 | 01; 05; 15 | Set flipflop 16 | X | X
Command flag | 153 | 154 | 01; 05; 15 | Reset flipflop 01 | X | X
Command flag | 154 | 155 | 01; 05; 15 | Reset flipflop 02 | X | X
Command flag | 155 | 156 | 01; 05; 15 | Reset flipflop 03 | X | X
Command flag | 156 | 157 | 01; 05; 15 | Reset flipflop 04 | X | X
Command flag | 157 | 158 | 01; 05; 15 | Reset flipflop 05 | X | X
Command flag | 158 | 159 | 01; 05; 15 | Reset flipflop 06 | X | X
Command flag | 159 | 160 | 01; 05; 15 | Reset flipflop 07 | X | X
Command flag | 160 | 161 | 01; 05; 15 | Reset flipflop 08 | X | X
Command flag | 161 | 162 | 01; 05; 15 | Reset flipflop 09 | X | X
Command flag | 162 | 163 | 01; 05; 15 | Reset flipflop 10 | X | X
Command flag | 163 | 164 | 01; 05; 15 | Reset flipflop 11 | X | X
Command flag | 164 | 165 | 01; 05; 15 | Reset flipflop 12 | X | X
Command flag | 165 | 166 | 01; 05; 15 | Reset flipflop 13 | X | X
Command flag | 166 | 167 | 01; 05; 15 | Reset flipflop 14 | X | X
Command flag | 167 | 168 | 01; 05; 15 | Reset flipflop 15 | X | X
Command flag | 168 | 169 | 01; 05; 15 | Reset flipflop 16 | X | X
Command flag | 169 | 170 | 01; 05; 15 | Toggle flipflop 01 | X | X
Command flag | 170 | 171 | 01; 05; 15 | Toggle flipflop 02 | X | X
Command flag | 171 | 172 | 01; 05; 15 | Toggle flipflop 03 | X | X
Command flag | 172 | 173 | 01; 05; 15 | Toggle flipflop 04 | X | X
Command flag | 173 | 174 | 01; 05; 15 | Toggle flipflop 05 | X | X
Command flag | 174 | 175 | 01; 05; 15 | Toggle flipflop 06 | X | X
Command flag | 175 | 176 | 01; 05; 15 | Toggle flipflop 07 | X | X
Command flag | 176 | 177 | 01; 05; 15 | Toggle flipflop 08 | X | X
Command flag | 177 | 178 | 01; 05; 15 | Toggle flipflop 09 | X | X
Command flag | 178 | 179 | 01; 05; 15 | Toggle flipflop 10 | X | X
Command flag | 179 | 180 | 01; 05; 15 | Toggle flipflop 11 | X | X
Command flag | 180 | 181 | 01; 05; 15 | Toggle flipflop 12 | X | X
Command flag | 181 | 182 | 01; 05; 15 | Toggle flipflop 13 | X | X
Command flag | 182 | 183 | 01; 05; 15 | Toggle flipflop 14 | X | X
Command flag | 183 | 184 | 01; 05; 15 | Toggle flipflop 15 | X | X
Command flag | 184 | 185 | 01; 05; 15 | Toggle flipflop 16 | X | X

## Discrete input contact (02)
Discrete input contact (02)
Function group | Modbus address | PLC address | Modbus function code | Controller function name | SOLAR | BATT
Digital input | 22500 | 122501 | 02 | Digital input 97 | X | X
Digital input | 22501 | 122502 | 02 | Digital input 96 | X | X
Digital input | 22502 | 122503 | 02 | Digital input 95 | X | X
Digital input | 22503 | 122504 | 02 | Digital input 94 | X | X
Digital input | 22504 | 122505 | 02 | Digital input 93 | X | X
Digital input | 22505 | 122506 | 02 | Digital input 92 | X | X
Digital input | 22506 | 122507 | 02 | Digital input 91 | X | X
Digital input | 22507 | 122508 | 02 | Digital input 133 | X | X
Digital input | 22508 | 122509 | 02 | Digital input 132 | X | X
Digital input | 22509 | 122510 | 02 | Digital input 131 | X | X
Digital input | 22510 | 122511 | 02 | Digital input 130 | X | X
Digital input | 22511 | 122512 | 02 | Digital input 129 | X | X
Digital input | 22512 | 122513 | 02 | Digital input 128 | X | X
Digital input | 22513 | 122514 | 02 | Digital input 127 | X | X
Digital input | 22514 | 122515 | 02 | Digital input 29 | X | X
Digital input | 22515 | 122516 | 02 | Digital input 30 | X | X
Digital input | 22516 | 122517 | 02 | Digital input 31 | X | X
Digital input | 22517 | 122518 | 02 | Digital input 32 | X | X
Digital input | 22518 | 122519 | 02 | Digital input 33 | X | X
Digital input | 22519 | 122520 | 02 | Digital input 34 | X | X
Digital input | 22520 | 122521 | 02 | Digital input 35 | X | X
Digital input | 22521 | 122522 | 02 | Digital input 65 | X | X
Digital input | 22522 | 122523 | 02 | Digital input 66 | X | X
Digital input | 22523 | 122524 | 02 | Digital input 67 | X | X
Digital input | 22524 | 122525 | 02 | Digital input 68 | X | X
Digital input | 22525 | 122526 | 02 | Digital input 69 | X | X
Digital input | 22526 | 122527 | 02 | Digital input 70 | X | X
Digital input | 22527 | 122528 | 02 | Digital input 71 | X | X
Digital input | 22528 | 122529 | 02 | Digital input 43 | X | X
Digital input | 22529 | 122530 | 02 | Digital input 44 | X | X
Digital input | 22530 | 122531 | 02 | Digital input 45 | X | X
Digital input | 22531 | 122532 | 02 | Digital input 46 | X | X
Digital input | 22532 | 122533 | 02 | Digital input 47 | X | X
Digital input | 22533 | 122534 | 02 | Digital input 48 | X | X
Digital input | 22534 | 122535 | 02 | Digital input 49 | X | X
Digital input | 22535 | 122536 | 02 | Digital input 50 | X | X
Digital input | 22536 | 122537 | 02 | Digital input 51 | X | X
Digital input | 22537 | 122538 | 02 | Digital input 52 | X | X
Digital input | 22538 | 122539 | 02 | Digital input 53 | X | X
Digital input | 22539 | 122540 | 02 | Digital input 54 | X | X
Digital input | 22540 | 122541 | 02 | Digital input 55 | X | X
Digital input | 22541 | 122542 | 02 | Digital input 23 | X | X
Digital input | 22583 | 122584 | 02 | Digital input 118 - Emergency stop | X | X
Digital input | 22584 | 122585 | 02 | Digital input 117 | X | X
Digital input | 22585 | 122586 | 02 | Digital input 116 | X | X
Digital input | 22586 | 122587 | 02 | Digital input 115 | X | X
Digital input | 22587 | 122588 | 02 | Digital input 114 | X | X
Digital input | 22588 | 122589 | 02 | Digital input 113 | X | X
Digital input | 22589 | 122590 | 02 | Digital input 112 | X | X
Digital input | 22591 | 122592 | 02 | Digital input 108 | X | X
Digital input | 22592 | 122593 | 02 | Digital input 105 | X | X
Digital input | 22593 | 122594 | 02 | Digital input 102 | X | X
Digital output | 23000 | 123001 | 02 | Relay 65 (M14.4) | X | X
Digital output | 23001 | 123002 | 02 | Relay 67 (M14.4) | X | X
Digital output | 23001 | 123002 | 02 | Relay 20 | X | X
Digital output | 23002 | 123003 | 02 | Relay 69 (M14.4) | X | X
Digital output | 23002 | 123003 | 02 | Relay 21 | X | X
Digital output | 23003 | 123004 | 02 | Relay 71 (M14.4) | X | X
Digital output | 23004 | 123005 | 02 | Relay 132 (M14.8) | X | X
Digital output | 23005 | 123006 | 02 | Relay 130 (M14.8) | X | X
Digital output | 23006 | 123007 | 02 | Relay 128 (M14.8) | X | X
Digital output | 23007 | 123008 | 02 | Relay 126 (M14.8) | X | X
Digital output | 23008 | 123009 | 02 | Relay 96 (M14.6) | X | X
Digital output | 23009 | 123010 | 02 | Relay 94 (M14.6) | X | X
Digital output | 23010 | 123011 | 02 | Relay 92 (M14.6) | X | X
Digital output | 23011 | 123012 | 02 | Relay 90 (M14.6) | X | X
Digital output | 23016 | 123017 | 02 | Relay 57 (M12) | X | X
Digital output | 23017 | 123018 | 02 | Relay 59 (M12) | X | X
Digital output | 23018 | 123019 | 02 | Relay 61 (M12) | X | X
Digital output | 23019 | 123020 | 02 | Relay 63 (M12) | X | X
Digital output | 23022 | 123023 | 02 | Any inhibit active (LED, DU2) | X | X
Digital output | 23025 | 123026 | 02 | Relay 5 | X | X
Digital output | 23047 | 123048 | 02 | Relay 69 (EF4) | X | X
Digital output | 23048 | 123049 | 02 | Relay 71 (EF4) | X | X
Digital output | 23053 | 123054 | 02 | LED CAN B | X | X
Digital output | 23054 | 123055 | 02 | LED CAN A | X | X
Digital output | 23055 | 123056 | 02 | LED USB | X | X

## Holding register (03;06;16)
Holding register (03;06;16)
Function group | Modbus address | Bit | PLC address | Modbus function code | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | SOLAR | BATT
Control command | 0 |  | 400001 | 03; 06; 16 | Power regulator setpoint - 0...100% of nominal power. Scale set in menu 7504. Activated in menu 7501 | INT16s | AB | 0 |  | X | X
Control command | 1 |  | 400002 | 03; 06; 16 | Cos phi regulator setpoint - 60...100 stated as cosPhi value/100. The value 100 means cosPhi = 1.00 Activated in menu 7502 | INT16s | AB | 0 |  | X | X
Control command | 2 |  | 400003 | 03; 06; 16 | Reactive power regulator setpoint - +/-100% of nominal power. A negative value means capacitive reactive power, and a positive value means inductive reactive power. Scale set in menu 7504. Activated in menu 7503 | INT16s | AB | 0 |  | X | X
Control command | 5 | 9 | 400006 | 03; 06; 16 | Alarm inhibit 3 | BOOL |  |  |  | X | X
Control command | 5 | 0 | 400006 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X
Control command | 5 | 1 | 400006 | 03; 06; 16 | Remote start | BOOL |  |  |  | X | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote ESB ON | BOOL |  |  |  |  | X
Control command | 5 | 2 | 400006 | 03; 06; 16 | Remote PVB ON | BOOL |  |  |  | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote ESB OFF | BOOL |  |  |  |  | X
Control command | 5 | 3 | 400006 | 03; 06; 16 | Remote PVB OFF | BOOL |  |  |  | X
Control command | 5 | 4 | 400006 | 03; 06; 16 | Remote stop | BOOL |  |  |  | X | X
Control command | 5 | 7 | 400006 | 03; 06; 16 | Alarm inhibit 1 | BOOL |  |  |  | X | X
Control command | 5 | 8 | 400006 | 03; 06; 16 | Alarm inhibit 2 | BOOL |  |  |  | X | X
Control command | 5 | 9 | 400006 | 03; 06; 16 | Alarm inhibit 3 | BOOL |  |  |  | X | X
Control command | 5 | 10 | 400006 | 03; 06; 16 | Alarm ack. | BOOL |  |  |  | X | X
Control command | 5 | 11 | 400006 | 03; 06; 16 | Nominal setting 1 | BOOL |  |  |  | X | X
Control command | 5 | 12 | 400006 | 03; 06; 16 | Nominal setting 2 | BOOL |  |  |  | X | X
Control command | 5 | 13 | 400006 | 03; 06; 16 | Nominal setting 3 | BOOL |  |  |  | X | X
Control command | 5 | 14 | 400006 | 03; 06; 16 | Nominal setting 4 | BOOL |  |  |  | X | X
Control command | 6 | 0 | 400007 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X
Control command | 6 | 1 | 400007 | 03; 06; 16 | Island | BOOL |  |  |  | X | X
Control command | 6 | 3 | 400007 | 03; 06; 16 | Peak shaving | BOOL |  |  |  | X | X
Control command | 6 | 4 | 400007 | 03; 06; 16 | Fixed power | BOOL |  |  |  | X | X
Control command | 6 | 5 | 400007 | 03; 06; 16 | Mains power export (MPE) | BOOL |  |  |  | X | X
Control command | 6 | 11 | 400007 | 03; 06; 16 | Auto start | BOOL |  |  |  | X | X
Control command | 6 | 12 | 400007 | 03; 06; 16 | Auto stop | BOOL |  |  |  | X | X
Control command | 6 | 13 | 400007 | 03; 06; 16 | Auto mode | BOOL |  |  |  | X | X
Control command | 6 | 14 | 400007 | 03; 06; 16 | Semi-Auto mode | BOOL |  |  |  | X | X
Control command | 6 | 15 | 400007 | 03; 06; 16 | Test mode | BOOL |  |  |  | X | X
Control command | 7 | 0 | 400008 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X
Control command | 7 | 3 | 400008 | 03; 06; 16 | External power control | BOOL |  |  |  | X | X
Control command | 7 | 4 | 400008 | 03; 06; 16 | External reactive power control | BOOL |  |  |  | X | X
Control command | 7 | 5 | 400008 | 03; 06; 16 | External power factor control | BOOL |  |  |  | X | X
Control command | 7 | 6 | 400008 | 03; 06; 16 | Capacitive PF | BOOL |  |  |  | X | X
Control command | 7 | 8 | 400008 | 03; 06; 16 | 1st priority | BOOL |  |  |  | X | X
Control command | 7 | 9 | 400008 | 03; 06; 16 | Application 1 | BOOL |  |  |  | X | X
Control command | 7 | 10 | 400008 | 03; 06; 16 | Application 2 | BOOL |  |  |  | X | X
Control command | 7 | 11 | 400008 | 03; 06; 16 | Application 3 | BOOL |  |  |  | X | X
Control command | 7 | 12 | 400008 | 03; 06; 16 | Application 4 | BOOL |  |  |  | X | X
Control command | 7 | 13 | 400008 | 03; 06; 16 | Battery test | BOOL |  |  |  | X | X
Control command | 7 | 15 | 400008 | 03; 06; 16 | Synchronise clock to 4:00 a.m. | BOOL |  |  |  | X | X
Control command | 8 | 0 | 400009 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X
Control command | 8 | 1 | 400009 | 03; 06; 16 | Virtual event 1 | BOOL |  |  |  | X | X
Control command | 8 | 2 | 400009 | 03; 06; 16 | Virtual event 2 | BOOL |  |  |  | X | X
Control command | 8 | 3 | 400009 | 03; 06; 16 | Virtual event 3 | BOOL |  |  |  | X | X
Control command | 8 | 4 | 400009 | 03; 06; 16 | Virtual event 4 | BOOL |  |  |  | X | X
Control command | 8 | 5 | 400009 | 03; 06; 16 | Virtual event 5 | BOOL |  |  |  | X | X
Control command | 8 | 6 | 400009 | 03; 06; 16 | Virtual event 6 | BOOL |  |  |  | X | X
Control command | 8 | 7 | 400009 | 03; 06; 16 | Virtual event 7 | BOOL |  |  |  | X | X
Control command | 8 | 8 | 400009 | 03; 06; 16 | Virtual event 8 | BOOL |  |  |  | X | X
Control command | 8 | 9 | 400009 | 03; 06; 16 | Virtual event 9 | BOOL |  |  |  | X | X
Control command | 8 | 10 | 400009 | 03; 06; 16 | Virtual event 10 | BOOL |  |  |  | X | X
Control command | 8 | 11 | 400009 | 03; 06; 16 | Virtual event 11 | BOOL |  |  |  | X | X
Control command | 8 | 12 | 400009 | 03; 06; 16 | Virtual event 12 | BOOL |  |  |  | X | X
Control command | 8 | 13 | 400009 | 03; 06; 16 | Virtual event 13 | BOOL |  |  |  | X | X
Control command | 8 | 14 | 400009 | 03; 06; 16 | Virtual event 14 | BOOL |  |  |  | X | X
Control command | 8 | 15 | 400009 | 03; 06; 16 | Virtual event 15 | BOOL |  |  |  | X | X
Control command | 9 | 0 | 400010 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X
Control command | 9 | 1 | 400010 | 03; 06; 16 | Virtual event 16 | BOOL |  |  |  | X | X
Control command | 9 | 2 | 400010 | 03; 06; 16 | Virtual event 17 | BOOL |  |  |  | X | X
Control command | 9 | 3 | 400010 | 03; 06; 16 | Virtual event 18 | BOOL |  |  |  | X | X
Control command | 9 | 4 | 400010 | 03; 06; 16 | Virtual event 19 | BOOL |  |  |  | X | X
Control command | 9 | 5 | 400010 | 03; 06; 16 | Virtual event 20 | BOOL |  |  |  | X | X
Control command | 9 | 6 | 400010 | 03; 06; 16 | Virtual event 21 | BOOL |  |  |  | X | X
Control command | 9 | 7 | 400010 | 03; 06; 16 | Virtual event 22 | BOOL |  |  |  | X | X
Control command | 9 | 8 | 400010 | 03; 06; 16 | Virtual event 23 | BOOL |  |  |  | X | X
Control command | 9 | 9 | 400010 | 03; 06; 16 | Virtual event 24 | BOOL |  |  |  | X | X
Control command | 9 | 10 | 400010 | 03; 06; 16 | Virtual event 25 | BOOL |  |  |  | X | X
Control command | 9 | 11 | 400010 | 03; 06; 16 | Virtual event 26 | BOOL |  |  |  | X | X
Control command | 9 | 12 | 400010 | 03; 06; 16 | Virtual event 27 | BOOL |  |  |  | X | X
Control command | 9 | 13 | 400010 | 03; 06; 16 | Virtual event 28 | BOOL |  |  |  | X | X
Control command | 9 | 14 | 400010 | 03; 06; 16 | Virtual event 29 | BOOL |  |  |  | X | X
Control command | 9 | 15 | 400010 | 03; 06; 16 | Virtual event 30 | BOOL |  |  |  | X | X
Control command | 10 | 0 | 400011 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X
Control command | 10 | 0 | 400011 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X
Control command | 10 | 1 | 400011 | 03; 06; 16 | Virtual event 31 | BOOL |  |  |  | X | X
Control command | 10 | 2 | 400011 | 03; 06; 16 | Virtual event 32 | BOOL |  |  |  | X | X
Control command | 10 | 4 | 400011 | 03; 06; 16 | Clear log | BOOL |  |  |  | X | X
Control command | 10 | 5 | 400011 | 03; 06; 16 | Clear Parameter edits | BOOL |  |  |  | X | X
Control command | 13 | 0 | 400014 | 03; 06; 16 | This bit must be 1 when writing the command word. If the bit is 0, the control command is ignored. | BOOL |  |  |  | X | X
Control command | 13 | 5 | 400014 | 03; 06; 16 | Enable external power control | BOOL |  |  |  | X | X
Control command | 13 | 6 | 400014 | 03; 06; 16 | Disable external power control | BOOL |  |  |  | X | X
Control command | 13 | 7 | 400014 | 03; 06; 16 | Enable external VAr control | BOOL |  |  |  | X | X
Control command | 13 | 8 | 400014 | 03; 06; 16 | Disable external VAr control | BOOL |  |  |  | X | X
Control command | 13 | 9 | 400014 | 03; 06; 16 | Enable external CosPhi control | BOOL |  |  |  | X | X
Control command | 13 | 10 | 400014 | 03; 06; 16 | Disable external CosPhi control | BOOL |  |  |  | X | X
Control command | 13 | 13 | 400014 | 03; 06; 16 | Reset horn | BOOL |  |  |  | X | X
Read area 1 (ASC to PLC/external system) | 40000 |  | 440001 | 03; 06; 16 | PV active power reference. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 40002 |  | 440003 | 03; 06; 16 | PV reactive power reference. | INT32s | ABCD | 0 | kVAr | X
Read area 1 (ASC to PLC/external system) | 40004 |  | 440005 | 03; 06; 16 | Emergency stop request to PV. 100: Activate emergency stop. 200: Deactivate emergency stop. | INT32s | ABCD | 0 |  | X
Read area 1 (ASC to PLC/external system) | 40008 |  | 440009 | 03; 06; 16 | Watch dog will increment continuously. To be used for PV/DEIF communication supervision on PV side. | INT32s | ABCD | 0 |  | X
Read area 1 (ASC to PLC/external system) | 40010 |  | 440011 | 03; 06; 16 | Active power delivered by the gensets. | INT32s | ABCD | 0 | kW* | X
Read area 1 (ASC to PLC/external system) | 40012 |  | 440013 | 03; 06; 16 | Online nominal genset power. | INT32s | ABCD | 0 | kW* | X
Read area 1 (ASC to PLC/external system) | 40014 |  | 440015 | 03; 06; 16 | Reactive power delivered by the gensets. | INT32s | ABCD | 0 | kVAr | X
Read area 1 (ASC to PLC/external system) | 40016 |  | 440017 | 03; 06; 16 | Minimum genset load required. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 40018 |  | 440019 | 03; 06; 16 | Mains active power. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 40020 |  | 440021 | 03; 06; 16 | Mains reactive power. | INT32s | ABCD | 0 | kVAr | X
Read area 1 (ASC to PLC/external system) | 40022 |  | 440023 | 03; 06; 16 | Amount of diesel used since last reset. | INT32s | ABCD | 0 | liter | X
Read area 1 (ASC to PLC/external system) | 40024 |  | 440025 | 03; 06; 16 | Diesel consumption. | INT32s | ABCD | 1 | liter/h | X
Read area 1 (ASC to PLC/external system) | 40026 |  | 440027 | 03; 06; 16 | PV active power reference. | INT16s | AB | 0 | % | X
Read area 1 (ASC to PLC/external system) | 40027 |  | 440028 | 03; 06; 16 | PV curtailment active. 0: Inactive. 1: Active | INT16s | AB | 0 |  | X
Read area 1 (ASC to PLC/external system) | 40028 |  | 440029 | 03; 06; 16 | Curtailed energy counter total. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40030 |  | 440031 | 03; 06; 16 | Curtailed energy counter month. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40032 |  | 440033 | 03; 06; 16 | Curtailed energy counter week. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40034 |  | 440035 | 03; 06; 16 | Curtailed energy counter day. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 40036 |  | 440037 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 40037 |  | 440038 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 40038 |  | 440039 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 40039 |  | 440040 | 03; 06; 16 | Plane of array irradiation sensor weighted | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 40040 |  | 440041 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 40041 |  | 440042 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 40042 |  | 440043 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 40042 |  | 440043 | 03; 06; 16 | Back of module temperature sensor weighted | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 40044 |  | 440045 | 03; 06; 16 | Instant maximum active power that can be generated by PV panels. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 40046 |  | 440047 | 03; 06; 16 | Instant maximum apparent power that can be generated by inverter(s). | INT32s | ABCD | 0 | kVA | X
Read area 1 (ASC to PLC/external system) | 40048 |  | 440049 | 03; 06; 16 | Instant maximum reactive power that can be generated by inverter(s) in first quadrant. | INT32s | ABCD | 0 | kVAr | X
Read area 1 (ASC to PLC/external system) | 40050 |  | 440051 | 03; 06; 16 | Instant maximum reactive power that can be generated by inverter(s) in fourth quadrant. | INT32s | ABCD | 0 | kVAr | X
Read area 1 (ASC to PLC/external system) | 40052 |  | 440053 | 03; 06; 16 | Active PV power production. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 40054 |  | 440055 | 03; 06; 16 | Active PV apparent power production. | INT32s | ABCD | 0 | kVA | X
Read area 1 (ASC to PLC/external system) | 40056 |  | 440057 | 03; 06; 16 | Active PV reactive power production. | INT32s | ABCD | 0 | kVAr | X
Read area 1 (ASC to PLC/external system) | 40058 |  | 440059 | 03; 06; 16 | Spinning reserve generated by this PV. | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 40060 |  | 440061 | 03; 06; 16 | Spinning reserve generated by all the PV’s | INT32s | ABCD | 0 | kW | X
Read area 1 (ASC to PLC/external system) | 40062 |  | 440063 | 03; 06; 16 | Global horizontal irradiation | INT16s | AB | 0 | W/m2 | X
Read area 1 (ASC to PLC/external system) | 40063 |  | 440064 | 03; 06; 16 | Ambient temperature | INT16s | AB | 1 | Deg C | X
Read area 1 (ASC to PLC/external system) | 40064 |  | 440065 | 03; 06; 16 | Relative humidity | INT16s | AB | 0 | % | X
Read area 1 (ASC to PLC/external system) | 40065 |  | 440066 | 03; 06; 16 | Barometric pressure | INT16s | AB | 0 | hPa | X
Read area 1 (ASC to PLC/external system) | 40066 |  | 440067 | 03; 06; 16 | Wind speed | INT16s | AB | 0 | m/s | X
Read area 1 (ASC to PLC/external system) | 40067 |  | 440068 | 03; 06; 16 | Wind direction | INT16s | AB | 0 | deg | X
Read area 1 (ASC to PLC/external system) | 40068 |  | 440069 | 03; 06; 16 | Rain fall | INT16s | AB | 0 | mm | X
Read area 1 (ASC to PLC/external system) | 40069 |  | 440070 | 03; 06; 16 | Snow depth | INT16s | AB | 0 | mm | X
Read area 1 (ASC to PLC/external system) | 40070 |  | 440071 | 03; 06; 16 | Curtailed energy counter year. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40072 |  | 440073 | 03; 06; 16 | Performance ratio total | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40073 |  | 440074 | 03; 06; 16 | Performance ratio year | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40074 |  | 440075 | 03; 06; 16 | Performance ratio month | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40075 |  | 440076 | 03; 06; 16 | Performance ratio week | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40076 |  | 440077 | 03; 06; 16 | Performance ratio day | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40077 |  | 440078 | 03; 06; 16 | Total genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40079 |  | 440080 | 03; 06; 16 | Yearly genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40081 |  | 440082 | 03; 06; 16 | Monthly genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40083 |  | 440084 | 03; 06; 16 | Weekly genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40085 |  | 440086 | 03; 06; 16 | Daily genset energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 1 (ASC to PLC/external system) | 40087 |  | 440088 | 03; 06; 16 | PV penetration total | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40088 |  | 440089 | 03; 06; 16 | Yearly PV penetration | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40089 |  | 440090 | 03; 06; 16 | Monthly PV penetration | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40090 |  | 440091 | 03; 06; 16 | Weekly PV penetration | INT16s | AB | 1 | % | X
Read area 1 (ASC to PLC/external system) | 40091 |  | 440092 | 03; 06; 16 | Daily PV penetration | INT16s | AB | 1 | % | X
Write area 1 (PLC/external system to ASC) | 40100 |  | 440101 | 03; 06; 16 | Available PV power. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_P_available will be used by logics. | INT32s | ABCD | 0 | kW* | X
Write area 1 (PLC/external system to ASC) | 40102 |  | 440103 | 03; 06; 16 | Active PV power. | INT32s | ABCD | 0 | kW* | X
Write area 1 (PLC/external system to ASC) | 40110 |  | 440111 | 03; 06; 16 | Available PV apparent power. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_S_available will be used by logics. | INT32s | ABCD | 0 | kVA* | X
Write area 1 (PLC/external system to ASC) | 40112 |  | 440113 | 03; 06; 16 | External PV spinning reserve request | INT32s | ABCD | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40114 |  | 440115 | 03; 06; 16 | Current operation mode of the PV plant: 200: Ready for operation | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 40116 |  | 440117 | 03; 06; 16 | Watch dog will increment continuously. To be used for PV/DEIF communication supervision on DEIF side. | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 40120 |  | 440121 | 03; 06; 16 | To raise warning and shutdown alarms on DEIF side 100: Warning. 200: Shutdown. 300: Warning & Shutdown. | INT32s | ABCD | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40122 |  | 440123 | 03; 06; 16 | Reactive PV power | INT32s | ABCD | 0 | kvar* | X
Write area 1 (PLC/external system to ASC) | 40124 |  | 440125 | 03; 06; 16 | Apparent PV power | INT32s | ABCD | 0 | kVA* | X
Write area 1 (PLC/external system to ASC) | 40128 |  | 440129 | 03; 06; 16 | Available PV reactive power in Q1. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q1 will be used by logics. | INT32s | ABCD | 0 | kVAr* | X
Write area 1 (PLC/external system to ASC) | 40130 |  | 440131 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 | X
Write area 1 (PLC/external system to ASC) | 40131 |  | 440132 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 | X
Write area 1 (PLC/external system to ASC) | 40132 |  | 440133 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 | X
Write area 1 (PLC/external system to ASC) | 40133 |  | 440134 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 1 | Deg C | X
Write area 1 (PLC/external system to ASC) | 40134 |  | 440135 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 1 | Deg C | X
Write area 1 (PLC/external system to ASC) | 40135 |  | 440136 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 1 | Deg C | X
Write area 1 (PLC/external system to ASC) | 40136 |  | 440137 | 03; 06; 16 | Global horizontal irradiation [W/m2] | INT16s | AB | 0 | W/m2 | X
Write area 1 (PLC/external system to ASC) | 40137 |  | 440138 | 03; 06; 16 | Ambient temperature [C] | INT16s | AB | 1 | Deg C | X
Write area 1 (PLC/external system to ASC) | 40138 |  | 440139 | 03; 06; 16 | Relative humidity [%] | INT16s | AB | 0 | % | X
Write area 1 (PLC/external system to ASC) | 40139 |  | 440140 | 03; 06; 16 | Barometric pressure [hPa] | INT16s | AB | 0 | hPa | X
Write area 1 (PLC/external system to ASC) | 40140 |  | 440141 | 03; 06; 16 | Wind speed [m/s] | INT16s | AB | 0 | m/s | X
Write area 1 (PLC/external system to ASC) | 40141 |  | 440142 | 03; 06; 16 | Wind direction [deg] | INT16s | AB | 0 | deg | X
Write area 1 (PLC/external system to ASC) | 40142 |  | 440143 | 03; 06; 16 | Rain fall [mm] | INT16s | AB | 0 | mm | X
Write area 1 (PLC/external system to ASC) | 40143 |  | 440144 | 03; 06; 16 | Snow depth [mm] | INT16s | AB | 0 | mm | X
Write area 1 (PLC/external system to ASC) | 40144 |  | 440145 | 03; 06; 16 | Available PV reactive power in Q2. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q2 will be used by logics. | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 40146 |  | 440147 | 03; 06; 16 | Available PV reactive power [kVAr*] in Q3. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q3 will be used by logics. | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 40148 |  | 440149 | 03; 06; 16 | Available PV reactive power [kVAr*] in Q4. <0: Nominal power setting in the ASC will be used by logics. >=0: PV_Q_available_Q4 will be used by logics. | INT32s | ABCD | 0 |  | X
Write area 1 (PLC/external system to ASC) | 40150 |  | 440151 | 03; 06; 16 | Active power of genset 1. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40151 |  | 440152 | 03; 06; 16 | Active power of genset 2. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40152 |  | 440153 | 03; 06; 16 | Active power of genset 3. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40153 |  | 440154 | 03; 06; 16 | Active power of genset 4. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40154 |  | 440155 | 03; 06; 16 | Active power of genset 5. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40155 |  | 440156 | 03; 06; 16 | Active power of genset 6. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40156 |  | 440157 | 03; 06; 16 | Active power of genset 7. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40157 |  | 440158 | 03; 06; 16 | Active power of genset 8. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40158 |  | 440159 | 03; 06; 16 | Active power of genset 9. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40159 |  | 440160 | 03; 06; 16 | Active power of genset 10. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40160 |  | 440161 | 03; 06; 16 | Active power of genset 11. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40161 |  | 440162 | 03; 06; 16 | Active power of genset 12. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40162 |  | 440163 | 03; 06; 16 | Active power of genset 13. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40163 |  | 440164 | 03; 06; 16 | Active power of genset 14. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40164 |  | 440165 | 03; 06; 16 | Active power of genset 15. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40165 |  | 440166 | 03; 06; 16 | Active power of genset 15. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40166 |  | 440167 | 03; 06; 16 | Reactive power of genset 1. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40167 |  | 440168 | 03; 06; 16 | Reactive power of genset 2. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40168 |  | 440169 | 03; 06; 16 | Reactive power of genset 3. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40169 |  | 440170 | 03; 06; 16 | Reactive power of genset 4. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40170 |  | 440171 | 03; 06; 16 | Reactive power of genset 5. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40171 |  | 440172 | 03; 06; 16 | Reactive power of genset 6. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40172 |  | 440173 | 03; 06; 16 | Reactive power of genset 7. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40173 |  | 440174 | 03; 06; 16 | Reactive power of genset 8. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40174 |  | 440175 | 03; 06; 16 | Reactive power of genset 9. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40175 |  | 440176 | 03; 06; 16 | Reactive power of genset 10. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40176 |  | 440177 | 03; 06; 16 | Reactive power of genset 11. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40177 |  | 440178 | 03; 06; 16 | Reactive power of genset 12. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40178 |  | 440179 | 03; 06; 16 | Reactive power of genset 13. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40179 |  | 440180 | 03; 06; 16 | Reactive power of genset 14. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40180 |  | 440181 | 03; 06; 16 | Reactive power of genset 15. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40181 |  | 440182 | 03; 06; 16 | Reactive power of genset 16. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40182 |  | 440183 | 03; 06; 16 | Active mains power. | INT16s | AB | 0 | kW | X
Write area 1 (PLC/external system to ASC) | 40183 |  | 440184 | 03; 06; 16 | Reactive mains power. | INT16s | AB | 0 | kvar | X
Write area 1 (PLC/external system to ASC) | 40184 |  | 440185 | 03; 06; 16 | GB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  | X
Write area 1 (PLC/external system to ASC) | 40185 |  | 440186 | 03; 06; 16 | MB closed feedback bitwise from genset 01..16 | INT16s | AB | 0 |  | X
Write area 1 (PLC/external system to ASC) | 40186 |  | 440187 | 03; 06; 16 | MB open feedback bitwise from genset 01..16 | INT16s | AB | 0 |  | X
Read area 2 (ASC to PLC/external system) | 40200 |  | 440201 | 03; 06; 16 | Total mains imported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40202 |  | 440203 | 03; 06; 16 | Yearly mains imported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40204 |  | 440205 | 03; 06; 16 | Monthly mains imported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40206 |  | 440207 | 03; 06; 16 | Weekly mains imported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40208 |  | 440209 | 03; 06; 16 | Daily mains imported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40210 |  | 440211 | 03; 06; 16 | Total mains exported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40212 |  | 440213 | 03; 06; 16 | Yearly mains exported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40214 |  | 440215 | 03; 06; 16 | Monthly mains exported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40216 |  | 440217 | 03; 06; 16 | Weekly mains exported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40218 |  | 440219 | 03; 06; 16 | Daily mains exported energy counter. | INT32s | ABCD | 0 | kWh | X
Read area 2 (ASC to PLC/external system) | 40220 |  | 440221 | 03; 06; 16 | PV power available and inteded for charging | INT32s | ABCD | 0 | kW | X
Read area 2 (ASC to PLC/external system) | 40222 |  | 440223 | 03; 06; 16 | Mains power available and inteded for charging | INT32s | ABCD | 0 | kW | X
Read area 2 (ASC to PLC/external system) | 40224 |  | 440225 | 03; 06; 16 | DG power available and inteded for charging | INT32s | ABCD | 0 | kW | X
Read area 2 (ASC to PLC/external system) | 40226 |  | 440227 | 03; 06; 16 | PV power charging active | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 40227 |  | 440228 | 03; 06; 16 | MAINS power charging active | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 40228 |  | 440229 | 03; 06; 16 | DG power charging active | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 40229 |  | 440230 | 03; 06; 16 | Power charging active | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 40230 |  | 440231 | 03; 06; 16 | Battery fully charged | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 40231 |  | 440232 | 03; 06; 16 | Energy source functionality OK | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 40232 |  | 440233 | 03; 06; 16 | Power source functionality OK | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 40233 |  | 440234 | 03; 06; 16 | FUNC MODE: 0: Dispatch only. 1: Power. 2: Energy. | INT16s | AB | 0 |  |  | X
Read area 2 (ASC to PLC/external system) | 40234 |  | 440235 | 03; 06; 16 | REG MODE: 0: Volt/Freq. 1: Droop. 2: P/Q | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40300 |  | 440301 | 03; 06; 16 | State of charge (SOC) | INT16s | AB | 0 | % |  | X
Read/Write (Battery) | 40301 |  | 440302 | 03; 06; 16 | State of energy (SOE) | INT32s | ABCD | 0 | kWh |  | X
Read/Write (Battery) | 40303 |  | 440304 | 03; 06; 16 | Full charged energy | INT32s | ABCD | 0 | kWh |  | X
Read/Write (Battery) | 40307 |  | 440308 | 03; 06; 16 | State of energy (SOE) TEMPCOMP | INT32s | ABCD | 0 | kWh |  | X
Read/Write (Battery) | 40309 |  | 440310 | 03; 06; 16 | Discharging capacity | INT32s | ABCD | 0 | kW |  | X
Read/Write (Battery) | 40311 |  | 440312 | 03; 06; 16 | Charging capacity | INT32s | ABCD | 0 | kW |  | X
Read/Write (Battery) | 40313 |  | 440314 | 03; 06; 16 | Apparent power capacity | INT32s | ABCD | 0 | kVA |  | X
Read/Write (Battery) | 40315 |  | 440316 | 03; 06; 16 | Frequency droop slope (Tesla: No decimals) | INT16s | AB | 1 | %P/Hz |  | X
Read/Write (Battery) | 40316 |  | 440317 | 03; 06; 16 | Voltage droop slope (Tesla: No decimals) | INT16s | AB | 1 | %Q/V |  | X
Read/Write (Battery) | 40317 |  | 440318 | 03; 06; 16 | State of health (SOH) | INT16s | AB | 0 | % |  | X
Read/Write (Battery) | 40318 |  | 440319 | 03; 06; 16 | BMS DC output voltage | INT16s | AB | 0 | Vdc |  | X
Read/Write (Battery) | 40319 |  | 440320 | 03; 06; 16 | Charging total | INT32s | ABCD | 1 | kWh |  | X
Read/Write (Battery) | 40321 |  | 440322 | 03; 06; 16 | Discharging total | INT32s | ABCD | 1 | kWh |  | X
Read/Write (Battery) | 40323 |  | 440324 | 03; 06; 16 | BMS state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40324 |  | 440325 | 03; 06; 16 | PCS state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40325 |  | 440326 | 03; 06; 16 | PCS DC input voltage from the battery | INT16s | AB | 1 | V |  | X
Read/Write (Battery) | 40326 |  | 440327 | 03; 06; 16 | DC current battery | INT16s | AB | 1 | A |  | X
Read/Write (Battery) | 40327 |  | 440328 | 03; 06; 16 | Temperature battery | INT16s | AB | 1 | Deg C |  | X
Read/Write (Battery) | 40328 |  | 440329 | 03; 06; 16 | Charge AH | INT32s | ABCD | 0 | kW |  | X
Read/Write (Battery) | 40330 |  | 440331 | 03; 06; 16 | Discharge AH | INT32s | ABCD | 0 | kW |  | X
Read/Write (Battery) | 40332 |  | 440333 | 03; 06; 16 | Energy absorbed | INT32s | ABCD | 0 | Wh |  | X
Read/Write (Battery) | 40334 |  | 440335 | 03; 06; 16 | Energy FED | INT32s | ABCD | 0 | Wh |  | X
Read/Write (Battery) | 40336 |  | 440337 | 03; 06; 16 | ESS Voltage L1-L2 | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 40337 |  | 440338 | 03; 06; 16 | ESS Voltage L2-L3 | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 40338 |  | 440339 | 03; 06; 16 | ESS Voltage L3-L1 | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 40339 |  | 440340 | 03; 06; 16 | ESS Voltage L1-N | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 40340 |  | 440341 | 03; 06; 16 | ESS Voltage L2-N | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 40341 |  | 440342 | 03; 06; 16 | ESS Voltage L3-N | INT16s | AB | 0 | V |  | X
Read/Write (Battery) | 40342 |  | 440343 | 03; 06; 16 | Frequency | INT16s | AB | 2 | Hz |  | X
Read/Write (Battery) | 40343 |  | 440344 | 03; 06; 16 | BCU/PCS alarm status | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40344 |  | 440345 | 03; 06; 16 | Max Charge voltage | INT16s | AB | 1 | V |  | X
Read/Write (Battery) | 40345 |  | 440346 | 03; 06; 16 | BMS max charge current | INT32s | AB | 2 | A |  | X
Read/Write (Battery) | 40347 |  | 440348 | 03; 06; 16 | min. discharge voltage | INT16s | AB | 1 | V |  | X
Read/Write (Battery) | 40348 |  | 440349 | 03; 06; 16 | max discharge current | INT32s | AB | 2 | A |  | X
Read/Write (Battery) | 40350 |  | 440351 | 03; 06; 16 | Inductive Q capacity | INT32s | ABCD | 0 | kvar |  | X
Read/Write (Battery) | 40352 |  | 440353 | 03; 06; 16 | Capacitive Q capacity | INT32s | ABCD | 0 | kvar |  | X
Read/Write (Battery) | 40354 |  | 440355 | 03; 06; 16 | External PDS/Sub-module 1 power | INT32s | ABCD | 1 | kW |  | X
Read/Write (Battery) | 40356 |  | 440357 | 03; 06; 16 | Internal PDS/Sub-module 2 power | INT32s | ABCD | 1 | kW |  | X
Read/Write (Battery) | 40358 |  | 440359 | 03; 06; 16 | PDS/Sub-module 1 state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40359 |  | 440360 | 03; 06; 16 | Sub-module 2 state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40360 |  | 440361 | 03; 06; 16 | BMS alarm status | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40361 |  | 440362 | 03; 06; 16 | PCS internal contactor state | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40362 |  | 440363 | 03; 06; 16 | BMS rack contactor state 0 = Open, 1 = Closed | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40364 |  | 440365 | 03; 06; 16 | Active power mode: 0 = Internal, 1 = P/Q mode, 2 = V/f mode, 3 = Droop, 0xFF = Unknown | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40365 |  | 440366 | 03; 06; 16 | ESS identifier | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40366 |  | 440367 | 03; 06; 16 | PCS DC current | INT32s | AB | 2 | A |  | X
Read/Write (Battery) | 40368 |  | 440369 | 03; 06; 16 | PDS alarm status | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40369 |  | 440370 | 03; 06; 16 | ESS configuration | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40370 |  | 440371 | 03; 06; 16 | BMS configuration | INT16s | AB | 0 |  |  | X
Read/Write (Battery) | 40371 |  | 440372 | 03; 06; 16 | Minimum battery cell voltage | INT16s | AB | 3 | V |  | X
Read/Write (Battery) | 40372 |  | 440373 | 03; 06; 16 | Average battery cell voltage | INT16s | AB | 3 | V |  | X
Read/Write (Battery) | 40373 |  | 440374 | 03; 06; 16 | Maximum battery cell voltage | INT16s | AB | 3 | V |  | X
Read/Write (Battery) | 40374 |  | 440375 | 03; 06; 16 | Minimum cell temperature | INT16s | AB | 1 | Deg C |  | X
Read/Write (Battery) | 40375 |  | 440376 | 03; 06; 16 | Average cell temperature | INT16s | AB | 1 | Deg C |  | X
Read/Write (Battery) | 40376 |  | 440377 | 03; 06; 16 | Maximum cell temperature | INT16s | AB | 1 | Deg C |  | X
Read/Write (Battery) | 40377 |  | 440378 | 03; 06; 16 | PCS fault flags | INT32u | AB | 0 |  |  | X
Read/Write (Battery) | 40379 |  | 440380 | 03; 06; 16 | PCS warning flags | INT32u | AB | 0 |  |  | X
Weather area | 40400 |  | 440401 | 03; 06; 16 | Weather serial number 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40401 |  | 440402 | 03; 06; 16 | Weather serial number 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40402 |  | 440403 | 03; 06; 16 | Weather serial number 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40403 |  | 440404 | 03; 06; 16 | Weather serial number 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40404 |  | 440405 | 03; 06; 16 | Weather serial number 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40405 |  | 440406 | 03; 06; 16 | Weather serial number 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40406 |  | 440407 | 03; 06; 16 | Weather serial number 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40407 |  | 440408 | 03; 06; 16 | Weather serial number 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40408 |  | 440409 | 03; 06; 16 | Weather serial number 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40409 |  | 440410 | 03; 06; 16 | Weather serial number 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40410 |  | 440411 | 03; 06; 16 | Weather serial number 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40411 |  | 440412 | 03; 06; 16 | Weather serial number 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40412 |  | 440413 | 03; 06; 16 | Weather serial number 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40413 |  | 440414 | 03; 06; 16 | Weather serial number 27-28 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40414 |  | 440415 | 03; 06; 16 | Weather serial number 29-30 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40415 |  | 440416 | 03; 06; 16 | Weather serial number 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40416 |  | 440417 | 03; 06; 16 | Weather model 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40417 |  | 440418 | 03; 06; 16 | Weather model 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40418 |  | 440419 | 03; 06; 16 | Weather model 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40419 |  | 440420 | 03; 06; 16 | Weather model 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40420 |  | 440421 | 03; 06; 16 | Weather model 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40421 |  | 440422 | 03; 06; 16 | Weather model 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40422 |  | 440423 | 03; 06; 16 | Weather model 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40423 |  | 440424 | 03; 06; 16 | Weather model 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40424 |  | 440425 | 03; 06; 16 | Weather model 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40425 |  | 440426 | 03; 06; 16 | Weather model 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40426 |  | 440427 | 03; 06; 16 | Weather model 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40427 |  | 440428 | 03; 06; 16 | Weather model 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40428 |  | 440429 | 03; 06; 16 | Weather model 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40429 |  | 440430 | 03; 06; 16 | Weather model 27-28 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40430 |  | 440431 | 03; 06; 16 | Weather model 29-30 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40431 |  | 440432 | 03; 06; 16 | Weather model 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
Weather area | 40432 |  | 440433 | 03; 06; 16 | Plane of array irradiation sensor 1 | INT16s | AB | 0 | W/m2 | X
Weather area | 40433 |  | 440434 | 03; 06; 16 | Plane of array irradiation sensor 2 | INT16s | AB | 0 | W/m2 | X
Weather area | 40434 |  | 440435 | 03; 06; 16 | Plane of array irradiation sensor 3 | INT16s | AB | 0 | W/m2 | X
Weather area | 40435 |  | 440436 | 03; 06; 16 | Plane of array irradiation sensor weighted | INT16s | AB | 0 | W/m2 | X
Weather area | 40436 |  | 440437 | 03; 06; 16 | Back of module temperature sensor 1 | INT16s | AB | 0 | Deg C | X
Weather area | 40437 |  | 440438 | 03; 06; 16 | Back of module temperature sensor 2 | INT16s | AB | 0 | Deg C | X
Weather area | 40438 |  | 440439 | 03; 06; 16 | Back of module temperature sensor 3 | INT16s | AB | 0 | Deg C | X
Weather area | 40439 |  | 440440 | 03; 06; 16 | Back of module temperature sensor weighted | INT16s | AB | 0 | Deg C | X
Weather area | 40440 |  | 440441 | 03; 06; 16 | Global horizontal irradiation | INT16s | AB | 0 | W/m2 | X
Weather area | 40441 |  | 440442 | 03; 06; 16 | Ambient temperature | INT16s | AB | 1 | Deg C | X
Weather area | 40442 |  | 440443 | 03; 06; 16 | Relative humidity | INT16s | AB | 0 | % | X
Weather area | 40443 |  | 440444 | 03; 06; 16 | Barometric pressure | INT16s | AB | 0 | hPa | X
Weather area | 40444 |  | 440445 | 03; 06; 16 | Wind speed | INT16s | AB | 0 | m/s | X
Weather area | 40445 |  | 440446 | 03; 06; 16 | Wind direction | INT16s | AB | 0 | deg | X
Weather area | 40446 |  | 440447 | 03; 06; 16 | Rain fall | INT16s | AB | 0 | mm | X
Weather area | 40447 |  | 440448 | 03; 06; 16 | Snow depth | INT16s | AB | 0 | mm | X
Weather area | 40448 |  | 440449 | 03; 06; 16 | Solar cell production 1 | INT16s | AB | 0 | W/m2 | X
Weather area | 40449 |  | 440450 | 03; 06; 16 | Solar cell production 2 | INT16s | AB | 0 | W/m2 | X
SunSpec 'C001': Common model | 50000 |  | 450001 | 03; 06; 16 | SunSpec ID 0x53756E53 | INT32u | ABCD | 0 |  | X
SunSpec 'C001': Common model | 50002 |  | 450003 | 03; 06; 16 | Model ID 1 | INT16s | AB | 0 |  | X
SunSpec 'C001': Common model | 50003 |  | 450004 | 03; 06; 16 | Data elements | INT16s | AB | 0 |  | X
SunSpec 'C001': Common model | 50004 |  | 450005 | 03; 06; 16 | Manufacturer 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50005 |  | 450006 | 03; 06; 16 | Manufacturer 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50006 |  | 450007 | 03; 06; 16 | Manufacturer 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50007 |  | 450008 | 03; 06; 16 | Manufacturer 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50008 |  | 450009 | 03; 06; 16 | Manufacturer 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50009 |  | 450010 | 03; 06; 16 | Manufacturer 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50010 |  | 450011 | 03; 06; 16 | Manufacturer 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50011 |  | 450012 | 03; 06; 16 | Manufacturer 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50012 |  | 450013 | 03; 06; 16 | Manufacturer 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50013 |  | 450014 | 03; 06; 16 | Manufacturer 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50014 |  | 450015 | 03; 06; 16 | Manufacturer 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50015 |  | 450016 | 03; 06; 16 | Manufacturer 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50016 |  | 450017 | 03; 06; 16 | Manufacturer 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50017 |  | 450018 | 03; 06; 16 | Manufacturer 27-28 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50018 |  | 450019 | 03; 06; 16 | Manufacturer 29-30 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50019 |  | 450020 | 03; 06; 16 | Manufacturer 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50020 |  | 450021 | 03; 06; 16 | Model 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50021 |  | 450022 | 03; 06; 16 | Model 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50022 |  | 450023 | 03; 06; 16 | Model 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50023 |  | 450024 | 03; 06; 16 | Model 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50024 |  | 450025 | 03; 06; 16 | Model 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50025 |  | 450026 | 03; 06; 16 | Model 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50026 |  | 450027 | 03; 06; 16 | Model 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50027 |  | 450028 | 03; 06; 16 | Model 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50028 |  | 450029 | 03; 06; 16 | Model 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50029 |  | 450030 | 03; 06; 16 | Model 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50030 |  | 450031 | 03; 06; 16 | Model 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50031 |  | 450032 | 03; 06; 16 | Model 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50032 |  | 450033 | 03; 06; 16 | Model 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50033 |  | 450034 | 03; 06; 16 | Model 27-28 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50034 |  | 450035 | 03; 06; 16 | Model 29-30 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50035 |  | 450036 | 03; 06; 16 | Model 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50036 |  | 450037 | 03; 06; 16 | Options 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50037 |  | 450038 | 03; 06; 16 | Options 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50038 |  | 450039 | 03; 06; 16 | Options 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50039 |  | 450040 | 03; 06; 16 | Options 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50040 |  | 450041 | 03; 06; 16 | Options 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50041 |  | 450042 | 03; 06; 16 | Options 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50042 |  | 450043 | 03; 06; 16 | Options 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50043 |  | 450044 | 03; 06; 16 | Options 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50044 |  | 450045 | 03; 06; 16 | Version 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50045 |  | 450046 | 03; 06; 16 | Version 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50046 |  | 450047 | 03; 06; 16 | Version 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50047 |  | 450048 | 03; 06; 16 | Version 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50048 |  | 450049 | 03; 06; 16 | Version 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50049 |  | 450050 | 03; 06; 16 | Version 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50050 |  | 450051 | 03; 06; 16 | Version 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50051 |  | 450052 | 03; 06; 16 | Version 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50052 |  | 450053 | 03; 06; 16 | Serial 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50053 |  | 450054 | 03; 06; 16 | Serial 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50054 |  | 450055 | 03; 06; 16 | Serial 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50055 |  | 450056 | 03; 06; 16 | Serial 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50056 |  | 450057 | 03; 06; 16 | Serial 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50057 |  | 450058 | 03; 06; 16 | Serial 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50058 |  | 450059 | 03; 06; 16 | Serial 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50059 |  | 450060 | 03; 06; 16 | Serial 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50060 |  | 450061 | 03; 06; 16 | Serial 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50061 |  | 450062 | 03; 06; 16 | Serial 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50062 |  | 450063 | 03; 06; 16 | Serial 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50063 |  | 450064 | 03; 06; 16 | Serial 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50064 |  | 450065 | 03; 06; 16 | Serial 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50065 |  | 450066 | 03; 06; 16 | Serial 27-28 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50066 |  | 450067 | 03; 06; 16 | Serial 29-30 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50067 |  | 450068 | 03; 06; 16 | Serial 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
SunSpec 'C001': Common model | 50068 |  | 450069 | 03; 06; 16 | Modbus ID 1 | INT16s | AB | 0 |  | X
SunSpec 'C001': Common model | 50069 |  | 450070 | 03; 06; 16 | Pad | INT16s | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50070 |  | 450071 | 03; 06; 16 | Model ID 103 | INT16u | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50071 |  | 450072 | 03; 06; 16 | Data elements 50 | INT16u | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50072 |  | 450073 | 03; 06; 16 | A | INT16u | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50073 |  | 450074 | 03; 06; 16 | AphA | INT16u | AB | 0 | A | X
SunSpec 'I103': Inverter model | 50074 |  | 450075 | 03; 06; 16 | AphB | INT16u | AB | 0 | A | X
SunSpec 'I103': Inverter model | 50075 |  | 450076 | 03; 06; 16 | AphC | INT16u | AB | 0 | A | X
SunSpec 'I103': Inverter model | 50076 |  | 450077 | 03; 06; 16 | A SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50077 |  | 450078 | 03; 06; 16 | PPVphAB | INT16u | AB | 0 | V | X
SunSpec 'I103': Inverter model | 50078 |  | 450079 | 03; 06; 16 | PPVphBC | INT16u | AB | 0 | V | X
SunSpec 'I103': Inverter model | 50079 |  | 450080 | 03; 06; 16 | PPVphCA | INT16u | AB | 0 | V | X
SunSpec 'I103': Inverter model | 50080 |  | 450081 | 03; 06; 16 | PVphA | sunssf | AB | 0 | V | X
SunSpec 'I103': Inverter model | 50081 |  | 450082 | 03; 06; 16 | PVphB | INT16u | AB | 0 | V | X
SunSpec 'I103': Inverter model | 50082 |  | 450083 | 03; 06; 16 | PVphC | INT16u | AB | 0 | V | X
SunSpec 'I103': Inverter model | 50083 |  | 450084 | 03; 06; 16 | V SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50084 |  | 450085 | 03; 06; 16 | W | INT16u | AB | 0 | kW | X
SunSpec 'I103': Inverter model | 50085 |  | 450086 | 03; 06; 16 | W SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50086 |  | 450087 | 03; 06; 16 | Hz | INT16u | AB | 0 | Hz | X
SunSpec 'I103': Inverter model | 50087 |  | 450088 | 03; 06; 16 | Hz SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50088 |  | 450089 | 03; 06; 16 | VA | INT16s | AB | 0 | kW | X
SunSpec 'I103': Inverter model | 50089 |  | 450090 | 03; 06; 16 | VA SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50090 |  | 450091 | 03; 06; 16 | VAr | INT16s | AB | 0 | kVAr | X
SunSpec 'I103': Inverter model | 50091 |  | 450092 | 03; 06; 16 | VAr SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50092 |  | 450093 | 03; 06; 16 | PF | INT16s | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50093 |  | 450094 | 03; 06; 16 | PF SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50094 |  | 450095 | 03; 06; 16 | WH | acc32 | ABCD | 0 | kWh | X
SunSpec 'I103': Inverter model | 50096 |  | 450097 | 03; 06; 16 | WH SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50097 |  | 450098 | 03; 06; 16 | DCA | INT16u | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50098 |  | 450099 | 03; 06; 16 | DCA SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50099 |  | 450100 | 03; 06; 16 | DCV | INT16u | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50100 |  | 450101 | 03; 06; 16 | DCV SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50101 |  | 450102 | 03; 06; 16 | DCW | INT16s | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50102 |  | 450103 | 03; 06; 16 | DCW SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50103 |  | 450104 | 03; 06; 16 | TmpCap | INT16s | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50104 |  | 450105 | 03; 06; 16 | TmpSnk | INT16s | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50105 |  | 450106 | 03; 06; 16 | TmpTrns | INT16s | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50106 |  | 450107 | 03; 06; 16 | TmpOt | INT16s | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50107 |  | 450108 | 03; 06; 16 | Tmp SF | sunssf | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50108 |  | 450109 | 03; 06; 16 | St | enum16 | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50109 |  | 450110 | 03; 06; 16 | StVnd | enum16 | AB | 0 |  | X
SunSpec 'I103': Inverter model | 50110 |  | 450111 | 03; 06; 16 | Evt1_HI | bitfield32 | ABCD | 0 |  | X
SunSpec 'I103': Inverter model | 50112 |  | 450113 | 03; 06; 16 | Evt2_HI | bitfield32 | ABCD | 0 |  | X
SunSpec 'I103': Inverter model | 50114 |  | 450115 | 03; 06; 16 | EvtVnd1 | bitfield32 | ABCD | 0 |  | X
SunSpec 'I103': Inverter model | 50116 |  | 450117 | 03; 06; 16 | EvtVnd2 | bitfield32 | ABCD | 0 |  | X
SunSpec 'I103': Inverter model | 50118 |  | 450119 | 03; 06; 16 | EvtVnd3 | bitfield32 | ABCD | 0 |  | X
SunSpec 'I103': Inverter model | 50120 |  | 450121 | 03; 06; 16 | EvtVnd4 | bitfield32 | ABCD | 0 |  | X
SunSpec 'I120': Name plate model | 50122 |  | 450123 | 03; 06; 16 | Model ID 120 | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50123 |  | 450124 | 03; 06; 16 | Data elements 26 | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50124 |  | 450125 | 03; 06; 16 | DERTyp 4 | enum16 | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50125 |  | 450126 | 03; 06; 16 | WRtg | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50126 |  | 450127 | 03; 06; 16 | WRtg SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50127 |  | 450128 | 03; 06; 16 | Data elements 26 | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50128 |  | 450129 | 03; 06; 16 | VARtg SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50129 |  | 450130 | 03; 06; 16 | VA1RtgQ1 | INT16s | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50130 |  | 450131 | 03; 06; 16 | VA1RtgQ2 | INT16s | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50131 |  | 450132 | 03; 06; 16 | VA1RtgQ3 | INT16s | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50132 |  | 450133 | 03; 06; 16 | VA1RtgQ4 | INT16s | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50133 |  | 450134 | 03; 06; 16 | VArRtg SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50134 |  | 450135 | 03; 06; 16 | ARtg | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50135 |  | 450136 | 03; 06; 16 | ARtg SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50136 |  | 450137 | 03; 06; 16 | PFRtgQ1 | INT16s | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50137 |  | 450138 | 03; 06; 16 | PFRtgQ2 | INT16s | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50138 |  | 450139 | 03; 06; 16 | PFRtgQ3 | INT16s | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50139 |  | 450140 | 03; 06; 16 | PFRtgQ4 | INT16s | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50140 |  | 450141 | 03; 06; 16 | PFRtg SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50141 |  | 450142 | 03; 06; 16 | WHRtg | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50142 |  | 450143 | 03; 06; 16 | WHRtg SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50143 |  | 450144 | 03; 06; 16 | AhrRtg | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50144 |  | 450145 | 03; 06; 16 | AhrRtg SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50145 |  | 450146 | 03; 06; 16 | MaxChaRte | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50146 |  | 450147 | 03; 06; 16 | MaxChaRte SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50147 |  | 450148 | 03; 06; 16 | MaxDisChaRte | INT16u | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50148 |  | 450149 | 03; 06; 16 | MaxDisChaRte SF | sunssf | AB | 0 |  | X
SunSpec 'I120': Name plate model | 50149 |  | 450150 | 03; 06; 16 | Pad | INT16s | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50150 |  | 450151 | 03; 06; 16 | Model ID 121 | INT16u | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50151 |  | 450152 | 03; 06; 16 | Data elements 30 | INT16u | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50153 |  | 450154 | 03; 06; 16 | VRef | INT16u | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50154 |  | 450155 | 03; 06; 16 | VRefOfs | INT16s | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50155 |  | 450156 | 03; 06; 16 | VMax | INT16u | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50156 |  | 450157 | 03; 06; 16 | VMin | INT16u | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50159 |  | 450160 | 03; 06; 16 | VArMaxQ2 | INT16s | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50160 |  | 450161 | 03; 06; 16 | VArMaxQ3 | INT16s | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50162 |  | 450163 | 03; 06; 16 | WGra | INT16u | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50163 |  | 450164 | 03; 06; 16 | PFMinQ1 | INT16s | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50164 |  | 450165 | 03; 06; 16 | PFMinQ2 | INT16s | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50165 |  | 450166 | 03; 06; 16 | PFMinQ3 | INT16s | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50166 |  | 450167 | 03; 06; 16 | PFMinQ4 | INT16s | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50167 |  | 450168 | 03; 06; 16 | VArAct | enum16 | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50168 |  | 450169 | 03; 06; 16 | ClcTotVA | enum16 | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50169 |  | 450170 | 03; 06; 16 | MaxRmpRte | INT16u | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50170 |  | 450171 | 03; 06; 16 | ECPNomHz | INT16u | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50171 |  | 450172 | 03; 06; 16 | ConnPh | enum16 | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50172 |  | 450173 | 03; 06; 16 | WMax SF | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50173 |  | 450174 | 03; 06; 16 | VA1RtgQ3 | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50174 |  | 450175 | 03; 06; 16 | VRef SF | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50175 |  | 450176 | 03; 06; 16 | VMinMax SF | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50176 |  | 450177 | 03; 06; 16 | VA SF | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50177 |  | 450178 | 03; 06; 16 | VAr SF | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50178 |  | 450179 | 03; 06; 16 | WGra SF | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50179 |  | 450180 | 03; 06; 16 | PFMin SF | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50180 |  | 450181 | 03; 06; 16 | MaxRmpRte SF | sunssf | AB | 0 |  | X
SunSpec 'I121': Inverter controls basic settings model | 50181 |  | 450182 | 03; 06; 16 | ECPNomHz SF | sunssf | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50182 |  | 450183 | 03; 06; 16 | Model ID 122 | INT16u | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50183 |  | 450184 | 03; 06; 16 | Data elements 44 | INT16u | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50184 |  | 450185 | 03; 06; 16 | PVConn | bitfield16 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50185 |  | 450186 | 03; 06; 16 | StorConn | bitfield16 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50186 |  | 450187 | 03; 06; 16 | ECPConn | bitfield16 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50187 |  | 450188 | 03; 06; 16 | ActWh | acc64 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50191 |  | 450192 | 03; 06; 16 | ActVAh | acc64 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50195 |  | 450196 | 03; 06; 16 | ActVArhQ1 | acc64 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50199 |  | 450200 | 03; 06; 16 | ActVArhQ2 | acc64 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50203 |  | 450204 | 03; 06; 16 | ActVArhQ3 | acc64 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50207 |  | 450208 | 03; 06; 16 | ActVArhQ4 | acc64 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50211 |  | 450212 | 03; 06; 16 | VArAval | int16s | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50212 |  | 450213 | 03; 06; 16 | VArAval SF | sunssf | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50213 |  | 450214 | 03; 06; 16 | WAval | int16u | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50214 |  | 450215 | 03; 06; 16 | WAval SF | sunssf | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50215 |  | 450216 | 03; 06; 16 | StSetLimMsk | bitfield32 | ABCD | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50217 |  | 450218 | 03; 06; 16 | StActCtl | bitfield32 | ABCD | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50219 |  | 450220 | 03; 06; 16 | TmSrc | string | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50220 |  | 450221 | 03; 06; 16 | TmSrc | string | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50221 |  | 450222 | 03; 06; 16 | TmSrc | string | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50222 |  | 450223 | 03; 06; 16 | TmSrc | string | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50223 |  | 450224 | 03; 06; 16 | Tms | int32u | ABCD | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50225 |  | 450226 | 03; 06; 16 | RtSt | bitfield16 | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50226 |  | 450227 | 03; 06; 16 | Ris | int16u | AB | 0 |  | X
SunSpec 'I122': Inverter controls extended measurements and status model | 50227 |  | 450228 | 03; 06; 16 | Ris SF | sunssf | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50228 |  | 450229 | 03; 06; 16 | Model ID 123 | INT16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50229 |  | 450230 | 03; 06; 16 | Data elements 24 | INT16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50230 |  | 450231 | 03; 06; 16 | Conn WinTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50231 |  | 450232 | 03; 06; 16 | Conn RvrtTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50234 |  | 450235 | 03; 06; 16 | WMaxLimPct WinTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50235 |  | 450236 | 03; 06; 16 | WMaxLimPct RvrtTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50236 |  | 450237 | 03; 06; 16 | WMaxLimPct RmpTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50239 |  | 450240 | 03; 06; 16 | OutPFSet WinTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50240 |  | 450241 | 03; 06; 16 | OutPFSet RvrtTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50241 |  | 450242 | 03; 06; 16 | OutPFSet RmpTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50246 |  | 450247 | 03; 06; 16 | VArPct WinTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50247 |  | 450248 | 03; 06; 16 | VArPct RvrtTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50248 |  | 450249 | 03; 06; 16 | VArPct RmpTms | int16u | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50251 |  | 450252 | 03; 06; 16 | WMaxLimPct SF | sunssf | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50252 |  | 450253 | 03; 06; 16 | OutPFSet SF | sunssf | AB | 0 |  | X
SunSpec 'I123': Immediate control model | 50253 |  | 450254 | 03; 06; 16 | VArPct SF | sunssf | AB | 0 |  | X
SunSpec 'E302': Irradiation model | 50254 |  | 450255 | 03; 06; 16 | Model ID 302 | INT16u | AB | 0 |  | X
SunSpec 'E302': Irradiation model | 50255 |  | 450256 | 03; 06; 16 | Data elements 5 | INT16u | AB | 0 |  | X
SunSpec 'E302': Irradiation model | 50256 |  | 450257 | 03; 06; 16 | GHI | INT16u | AB | 0 |  | X
SunSpec 'E302': Irradiation model | 50257 |  | 450258 | 03; 06; 16 | POAI | INT16u | AB | 0 |  | X
SunSpec 'E302': Irradiation model | 50258 |  | 450259 | 03; 06; 16 | DFI | INT16u | AB | 0 |  | X
SunSpec 'E302': Irradiation model | 50259 |  | 450260 | 03; 06; 16 | DNI | INT16u | AB | 0 |  | X
SunSpec 'E302': Irradiation model | 50260 |  | 450261 | 03; 06; 16 | OTI | INT16u | AB | 0 |  | X
SunSpec 'E303': Back of module temperature model | 50261 |  | 450262 | 03; 06; 16 | Model ID 303 | INT16u | AB | 0 |  | X
SunSpec 'E303': Back of module temperature model | 50262 |  | 450263 | 03; 06; 16 | Data elements 3 | INT16u | AB | 0 |  | X
SunSpec 'E303': Back of module temperature model | 50263 |  | 450264 | 03; 06; 16 | BOM1 | INT16s | AB | 0 |  | X
SunSpec 'E303': Back of module temperature model | 50264 |  | 450265 | 03; 06; 16 | BOM2 | INT16s | AB | 0 |  | X
SunSpec 'E303': Back of module temperature model | 50265 |  | 450266 | 03; 06; 16 | BOM3 | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50266 |  | 450267 | 03; 06; 16 | Model ID 307 | INT16u | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50267 |  | 450268 | 03; 06; 16 | Data elements 11 | INT16u | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50268 |  | 450269 | 03; 06; 16 | TmpAmb | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50269 |  | 450270 | 03; 06; 16 | RH | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50270 |  | 450271 | 03; 06; 16 | Pres | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50271 |  | 450272 | 03; 06; 16 | WndSpd | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50272 |  | 450273 | 03; 06; 16 | WndDir | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50273 |  | 450274 | 03; 06; 16 | Rain | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50274 |  | 450275 | 03; 06; 16 | Snw | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50275 |  | 450276 | 03; 06; 16 | PPT | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50276 |  | 450277 | 03; 06; 16 | ElecFld | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50277 |  | 450278 | 03; 06; 16 | SurWet | INT16s | AB | 0 |  | X
SunSpec 'E307': Base meteorological model | 50278 |  | 450279 | 03; 06; 16 | SoilWet | INT16s | AB | 0 |  | X
SunSpec 'End model' | 50279 |  | 450280 | 03; 06; 16 | Model ID 0xFFFF | INT16u | AB | 0 |  | X
SunSpec 'End model' | 50280 |  | 450281 | 03; 06; 16 | Data elements 0 | INT16u | AB | 0 |  | X
Control time command | 58000 |  | 458001 | 03; 06; 16 | Year (2003-2099) | INT16s | AB | 0 |  | X | X
Control time command | 58001 |  | 458002 | 03; 06; 16 | Month (1-12) | INT16s | AB | 0 |  | X | X
Control time command | 58002 |  | 458003 | 03; 06; 16 | Date (1-31) | INT16s | AB | 0 |  | X | X
Control time command | 58003 |  | 458004 | 03; 06; 16 | Day (1-7, Monday - Sunday) | INT16s | AB | 0 |  | X | X
Control time command | 58004 |  | 458005 | 03; 06; 16 | Hour (0-23) | INT16s | AB | 0 |  | X | X
Control time command | 58005 |  | 458006 | 03; 06; 16 | Min (0-59) | INT16s | AB | 0 |  | X | X
Control time command | 58006 |  | 458007 | 03; 06; 16 | Sec (0-59) | INT16s | AB | 0 |  | X | X

## Input register (04)
Input register (04)
Function group | Modbus address | Bit | PLC address | Modbus function code | Channel | Controller function name | Data type | Data format | Scaling (10⁻ˣ) | Unit | SOLAR | BATT
APPL version | 500 |  | 300501 | 04 |  | Application version | INT16s | AB | 0 |  | X | X
AC measurement | 501 |  | 300502 | 04 |  | PV/ESS Voltage L1-L2 | INT16s | AB | 0 | V | X | X
AC measurement | 502 |  | 300503 | 04 |  | PV/ESS Voltage L2-L3 | INT16s | AB | 0 | V | X | X
AC measurement | 503 |  | 300504 | 04 |  | PV/ESS Voltage L3-L1 | INT16s | AB | 0 | V | X | X
AC measurement | 504 |  | 300505 | 04 |  | PV/ESS Voltage L1-N | INT16s | AB | 0 | V | X | X
AC measurement | 505 |  | 300506 | 04 |  | PV/ESS Voltage L2-N | INT16s | AB | 0 | V | X | X
AC measurement | 506 |  | 300507 | 04 |  | PV/ESS Voltage L3-N | INT16s | AB | 0 | V | X | X
AC measurement | 507 |  | 300508 | 04 |  | PV/ESS Frequency L1 | INT16s | AB | 2 | Hz | X | X
AC measurement | 508 |  | 300509 | 04 |  | PV/ESS Frequency L2 | INT16s | AB | 2 | Hz | X | X
AC measurement | 509 |  | 300510 | 04 |  | PV/ESS Frequency L3 | INT16s | AB | 2 | Hz | X | X
AC measurement | 510 |  | 300511 | 04 |  | PV/ESS Voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X | X
AC measurement | 511 |  | 300512 | 04 |  | PV/ESS Voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X | X
AC measurement | 512 |  | 300513 | 04 |  | PV/ESS Voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X | X
AC measurement | 513 |  | 300514 | 04 |  | PV/ESS Current L1 | INT16s | AB | 0 | A | X | X
AC measurement | 514 |  | 300515 | 04 |  | PV/ESS Current L2 | INT16s | AB | 0 | A | X | X
AC measurement | 515 |  | 300516 | 04 |  | PV/ESS Current L3 | INT16s | AB | 0 | A | X | X
AC measurement | 516 |  | 300517 | 04 |  | PV/ESS Power L1 | INT16s | AB | 0 | kW | X | X
AC measurement | 517 |  | 300518 | 04 |  | PV/ESS Power L2 | INT16s | AB | 0 | kW | X | X
AC measurement | 518 |  | 300519 | 04 |  | PV/ESS Power L3 | INT16s | AB | 0 | kW | X | X
AC measurement | 519 |  | 300520 | 04 |  | PV/ESS Power | INT16s | AB | 0 | kW | X | X
AC measurement | 520 |  | 300521 | 04 |  | PV/ESS Reactive power L1 | INT16s | AB | 0 | kVAr | X | X
AC measurement | 521 |  | 300522 | 04 |  | PV/ESS Reactive power L2 | INT16s | AB | 0 | kVAr | X | X
AC measurement | 522 |  | 300523 | 04 |  | PV/ESS Reactive power L3 | INT16s | AB | 0 | kVAr | X | X
AC measurement | 523 |  | 300524 | 04 |  | PV/ESS Reactive power | INT16s | AB | 0 | kVAr | X | X
AC measurement | 524 |  | 300525 | 04 |  | PV/ESS Apparent power L1 | INT16s | AB | 0 | kVA | X | X
AC measurement | 525 |  | 300526 | 04 |  | PV/ESS Apparent power L2 | INT16s | AB | 0 | kVA | X | X
AC measurement | 526 |  | 300527 | 04 |  | PV/ESS Apparent power L3 | INT16s | AB | 0 | kVA | X | X
AC measurement | 527 |  | 300528 | 04 |  | PV/ESS Apparent power | INT16s | AB | 0 | kVA | X | X
Counter | 528 |  | 300529 | 04 |  | Q: Export reactive energy counter, total | INT32s | ABCD | 0 | kVArh | X | X
Counter | 530 |  | 300531 | 04 |  | P: Export, active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 532 |  | 300533 | 04 |  | P: Export, active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 534 |  | 300535 | 04 |  | P: Export, active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 536 |  | 300537 | 04 |  | P: Export, active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
AC measurement | 538 |  | 300539 | 04 |  | Power factor | INT16s | AB | 2 | PF | X | X
AC measurement | 539 |  | 300540 | 04 |  | BB voltage L1-L2 | INT16s | AB | 0 | V | X | X
AC measurement | 540 |  | 300541 | 04 |  | BB voltage L2-L3 | INT16s | AB | 0 | V | X | X
AC measurement | 541 |  | 300542 | 04 |  | BB voltage L3-L1 | INT16s | AB | 0 | V | X | X
AC measurement | 542 |  | 300543 | 04 |  | BB voltage L1-N | INT16s | AB | 0 | V | X | X
AC measurement | 543 |  | 300544 | 04 |  | BB voltage L2-N | INT16s | AB | 0 | V | X | X
AC measurement | 544 |  | 300545 | 04 |  | BB voltage L3-N | INT16s | AB | 0 | V | X | X
AC measurement | 545 |  | 300546 | 04 |  | BB frequency L1 | INT16s | AB | 2 | Hz | X | X
AC measurement | 546 |  | 300547 | 04 |  | BB frequency L2 | INT16s | AB | 2 | Hz | X | X
AC measurement | 547 |  | 300548 | 04 |  | BB frequency L3 | INT16s | AB | 2 | Hz | X | X
AC measurement | 548 |  | 300549 | 04 |  | BB voltage phase angle L1-L2 | INT16s | AB | 1 | Deg | X | X
AC measurement | 549 |  | 300550 | 04 |  | BB voltage phase angle L2-L3 | INT16s | AB | 1 | Deg | X | X
AC measurement | 550 |  | 300551 | 04 |  | BB voltage phase angle L3-L1 | INT16s | AB | 1 | Deg | X | X
AC measurement | 551 |  | 300552 | 04 |  | U BB L1 - U PV/ESS L1 phase angle | INT16s | AB | 1 | Deg | X | X
AC measurement | 552 |  | 300553 | 04 |  | U BB L2 - U PV/ESS L2 phase angle | INT16s | AB | 1 | Deg | X | X
AC measurement | 553 |  | 300554 | 04 |  | U BB L3 - U PV/ESS L3 phase angle | INT16s | AB | 1 | Deg | X | X
Counter | 554 |  | 300555 | 04 |  | Running hours | INT32s | ABCD | 0 |  | X | X
Counter | 558 |  | 300559 | 04 |  | No. of alarms | INT16s | AB | 0 |  | X | X
Counter | 559 |  | 300560 | 04 |  | No. of unacknowledged alarms | INT16s | AB | 0 |  | X | X
Counter | 560 |  | 300561 | 04 |  | No. of active acknowledged alarms | INT16s | AB | 0 |  | X | X
Counter | 563 |  | 300564 | 04 |  | No. of ESB operations | INT16s | AB | 0 |  |  | X
Counter | 563 |  | 300564 | 04 |  | No. of CB operations | INT16s | AB | 0 |  | X
DC measurement | 567 |  | 300568 | 04 |  | DC supply term. 1-2 | INT16s | AB | 1 | V | X | X
AC measurement | 573 |  | 300574 | 04 |  | Cos-phi | INT16s | AB | 2 | cosPhi | X | X
AC measurement | 574 |  | 300575 | 04 |  | Cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 |  | X | X
DC measurement | 583 |  | 300584 | 04 |  | Multi-input 102 | INT16s | AB | 0 |  | X | X
DC measurement | 584 |  | 300585 | 04 |  | Multi-input 105 | INT16s | AB | 0 |  | X | X
DC measurement | 585 |  | 300586 | 04 |  | Multi-input 108 | INT16s | AB | 0 |  | X | X
DC measurement | 586 |  | 300587 | 04 |  | Analogue input 91 | INT16s | AB | 0 |  | X | X
DC measurement | 587 |  | 300588 | 04 |  | Analogue input 93 | INT16s | AB | 0 |  | X | X
DC measurement | 588 |  | 300589 | 04 |  | Analogue input 95 | INT16s | AB | 0 |  | X | X
DC measurement | 589 |  | 300590 | 04 |  | Analogue input 97 | INT16s | AB | 0 |  | X | X
DC measurement | 590 |  | 300591 | 04 |  | Internal Temperature | INT16s | AB | 1 | Deg C | X | X
AC measurement | 592 |  | 300593 | 04 |  | Mains P total | INT16s | AB | 0 | kW | X | X
AC measurement | 593 |  | 300594 | 04 |  | PV P Reference | INT16s | AB | 0 | kW | X | X
AC measurement | 594 |  | 300595 | 04 |  | PV P Reference Ramped incl ClosedLoop | INT16s | AB | 0 | kW | X | X
AC measurement | 595 |  | 300596 | 04 |  | PV Q Reference | INT16s | AB | 0 | kW | X | X
AC measurement | 596 |  | 300597 | 04 |  | PV Q Reference Ramped | INT16s | AB | 0 | kW | X | X
AC measurement | 599 |  | 300600 | 04 |  | Any ext. mains on busbar - Open PMS | INT16s | AB | 0 |  | X | X
AC measurement | 600 |  | 300601 | 04 |  | Any local ext. mains on busbar - Open PMS | INT16s | AB | 0 |  | X | X
AC measurement | 601 |  | 300602 | 04 |  | Any ext. DG on busbar - Open PMS | INT16s | AB | 0 |  | X | X
AC measurement | 602 |  | 300603 | 04 |  | Any local ext. DG on busbar - Open PMS | INT16s | AB | 0 |  | X | X
Control command state | 642 |  | 300643 | 04 |  | Control command address 0 | INT16s | AB | 0 |  | X | X
Control command state | 643 |  | 300644 | 04 |  | Control command address 1 | INT16s | AB | 0 |  | X | X
Control command state | 644 |  | 300645 | 04 |  | Control command address 2 | INT16s | AB | 0 |  | X | X
Control command state | 645 |  | 300646 | 04 |  | Control command address 3 | INT16s | AB | 0 |  | X | X
Control command state | 646 |  | 300647 | 04 |  | Control command address 4 | INT16s | AB | 0 |  | X | X
Control command state | 647 |  | 300648 | 04 |  | Control command address 5 | INT16s | AB | 0 |  | X | X
Control command state | 648 |  | 300649 | 04 |  | Control command address 6 | INT16s | AB | 0 |  | X | X
Control command state | 649 |  | 300650 | 04 |  | Control command address 7 | INT16s | AB | 0 |  | X | X
Control command state | 650 |  | 300651 | 04 |  | Control command address 8 | INT16s | AB | 0 |  | X | X
Control command state | 651 |  | 300652 | 04 |  | Control command address 9 | INT16s | AB | 0 |  | X | X
Control command state | 652 |  | 300653 | 04 |  | Control command address 10 | INT16s | AB | 0 |  | X | X
Control command state | 653 |  | 300654 | 04 |  | Control command address 11 | INT16s | AB | 0 |  | X | X
Control command state | 654 |  | 300655 | 04 |  | Control command address 12 | INT16s | AB | 0 |  | X | X
Control command state | 655 |  | 300656 | 04 |  | Control command address 13 | INT16s | AB | 0 |  | X | X
DC measurement | 656 |  | 300657 | 04 |  | Analogue input 127 | INT16s | AB | 0 |  | X | X
DC measurement | 657 |  | 300658 | 04 |  | Analogue input 129 | INT16s | AB | 0 |  | X | X
DC measurement | 658 |  | 300659 | 04 |  | Analogue input 131 | INT16s | AB | 0 |  | X | X
DC measurement | 659 |  | 300660 | 04 |  | Analogue input 133 | INT16s | AB | 0 |  | X | X
AC measurement | 669 |  | 300670 | 04 |  | Mains Q Power | INT16s | AB | 0 | kvar | X | X
AC measurement | 670 |  | 300671 | 04 |  | Mains cos-phi | INT16s | AB | 0 |  | X | X
AC measurement | 671 |  | 300672 | 04 |  | Mains cos-phi Inductive/Capacitive 0=Inductive, 1=Capacitive | INT16s | AB | 0 | kW | X | X
AC measurement | 672 |  | 300673 | 04 |  | Mains Q in STAND-ALONE. 0=OFF, 1=ON | INT16s | AB | 0 | kW | X | X
AC measurement | 700 |  | 300701 | 04 |  | Instant P Max (power derated) | INT16s | AB | 0 | kW | X | X
AC measurement | 701 |  | 300702 | 04 |  | Mains P in STAND-ALONE. 0=OFF, 1=ON | INT16s | AB | 0 | kW | X | X
AC measurement | 721 |  | 300722 | 04 |  | Total available power in PMS | INT16s | AB | 0 | kW | X | X
AC measurement | 722 |  | 300723 | 04 |  | Spinning reserve request ALC | INT16s | AB | 0 | kW | X | X
AC measurement | 723 |  | 300724 | 04 |  | Spinning reserve request ASC | INT16s | AB | 0 | kW | X | X
Counter | 790 |  | 300791 | 04 |  | Q: Export reactive energy counter, month | INT32s | ABCD | 0 | kVArh | X | X
Counter | 792 |  | 300793 | 04 |  | Q: Export reactive energy counter, week | INT32s | ABCD | 0 | kVArh | X | X
Counter | 794 |  | 300795 | 04 |  | Q: Export reactive energy counter, day | INT32s | ABCD | 0 | kVArh | X | X
Counter | 796 |  | 300797 | 04 |  | P: Import active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
Counter | 798 |  | 300799 | 04 |  | P: Import active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 800 |  | 300801 | 04 |  | P: Import active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 802 |  | 300803 | 04 |  | P: Import active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 804 |  | 300805 | 04 |  | Q: Import reactive energy counter, total | INT32s | ABCD | 0 | kVArh | X | X
Counter | 806 |  | 300807 | 04 |  | Q: Import reactive energy counter, month | INT32s | ABCD | 0 | kVArh | X | X
Counter | 808 |  | 300809 | 04 |  | Q: Import reactive energy counter, week | INT32s | ABCD | 0 | kVArh | X | X
Counter | 810 |  | 300811 | 04 |  | Q: Import reactive energy counter, day | INT32s | ABCD | 0 | kVArh | X | X
Counter | 812 |  | 300813 | 04 |  | Pulse counter 01 | INT32s | ABCD | 0 |  | X | X
Counter | 814 |  | 300815 | 04 |  | Pulse counter 02 | INT32s | ABCD | 0 |  | X | X
Counter | 852 |  | 300853 | 04 |  | Mains P: Export active energy counter, year | INT32s | ABCD | 0 | kWh | X | X
Counter | 854 |  | 300855 | 04 |  | Mains P: Export active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
Counter | 856 |  | 300857 | 04 |  | Mains P: Export active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 858 |  | 300859 | 04 |  | Mains P: Export active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 860 |  | 300861 | 04 |  | Mains P: Export active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 862 |  | 300863 | 04 |  | Mains P: Import active energy counter, year | INT32s | ABCD | 0 | kWh | X | X
Counter | 864 |  | 300865 | 04 |  | Mains P: Import active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
Counter | 866 |  | 300867 | 04 |  | Mains P: Import active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 868 |  | 300869 | 04 |  | Mains P: Import active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 870 |  | 300871 | 04 |  | Mains P: Import active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 872 |  | 300873 | 04 |  | DG P: Produced active energy counter, year | INT32s | ABCD | 0 | kWh | X | X
Counter | 874 |  | 300875 | 04 |  | DG P: Produced active energy counter, total | INT32s | ABCD | 0 | kWh | X | X
Counter | 876 |  | 300877 | 04 |  | DG P: Produced active energy counter, month | INT32s | ABCD | 0 | kWh | X | X
Counter | 878 |  | 300879 | 04 |  | DG P: Produced active energy counter, week | INT32s | ABCD | 0 | kWh | X | X
Counter | 880 |  | 300881 | 04 |  | DG P: Produced active energy counter, day | INT32s | ABCD | 0 | kWh | X | X
Counter | 882 |  | 300883 | 04 |  | P: Export active energy counter, year | INT32s | ABCD | 0 | kVArh | X | X
Counter | 884 |  | 300885 | 04 |  | Q: Export reactive energy counter, year | INT32s | ABCD | 0 | kVArh | X | X
Counter | 886 |  | 300887 | 04 |  | P: Import active energy counter, year | INT32s | ABCD | 0 | kVArh | X | X
Counter | 888 |  | 300889 | 04 |  | Q: Import reactive energy counter, year | INT32s | ABCD | 0 | kWh | X | X
AC measurement | 890 |  | 300891 | 04 |  | P curtailed energy year | INT32s | ABCD | 0 | kWh | X | X
AC measurement | 892 |  | 300893 | 04 |  | P curtailed energy total | INT32s | ABCD | 0 | kWh | X | X
AC measurement | 894 |  | 300895 | 04 |  | P curtailed energy month | INT32s | ABCD | 0 | kWh | X | X
AC measurement | 896 |  | 300897 | 04 |  | P curtailed energy week | INT32s | ABCD | 0 | kWh | X | X
AC measurement | 898 |  | 300899 | 04 |  | P curtailed energy day | INT32s | ABCD | 0 | kWh | X | X
AC alarm | 1000 | 0 | 301001 | 04 | 1000 | PV/ESS -P> 1 | BOOL |  |  |  | X | X
AC alarm | 1000 | 1 | 301001 | 04 | 1010 | PV/ESS -P> 2 | BOOL |  |  |  | X | X
AC alarm | 1000 | 3 | 301001 | 04 | 1030 | PV/ESS I> 1 | BOOL |  |  |  | X | X
AC alarm | 1000 | 4 | 301001 | 04 | 1040 | PV/ESS I> 2 | BOOL |  |  |  | X | X
AC alarm | 1000 | 5 | 301001 | 04 | 1050 | PV/ESS I> 3 | BOOL |  |  |  | X | X
AC alarm | 1000 | 6 | 301001 | 04 | 1060 | PV/ESS I> 4 | BOOL |  |  |  | X | X
AC alarm | 1000 | 9 | 301001 | 04 | 1130 | PV/ESS I>> 1 | BOOL |  |  |  | X | X
AC alarm | 1000 | 10 | 301001 | 04 | 1140 | PV/ESS I>> 2 | BOOL |  |  |  | X | X
AC alarm | 1000 | 11 | 301001 | 04 | 1150 | PV/ESS U> 1 | BOOL |  |  |  | X | X
AC alarm | 1000 | 12 | 301001 | 04 | 1160 | PV/ESS U> 2 | BOOL |  |  |  | X | X
AC alarm | 1000 | 13 | 301001 | 04 | 1170 | PV/ESS U< 1 | BOOL |  |  |  | X | X
AC alarm | 1000 | 14 | 301001 | 04 | 1180 | PV/ESS U< 2 | BOOL |  |  |  | X | X
AC alarm | 1000 | 15 | 301001 | 04 | 1190 | PV/ESS U< 3 | BOOL |  |  |  | X | X
AC alarm | 1001 | 0 | 301002 | 04 | 1210 | PV/ESS f> 1 | BOOL |  |  |  | X | X
AC alarm | 1001 | 1 | 301002 | 04 | 1220 | PV/ESS f> 2 | BOOL |  |  |  | X | X
AC alarm | 1001 | 2 | 301002 | 04 | 1230 | PV/ESS f> 3 | BOOL |  |  |  | X | X
AC alarm | 1001 | 3 | 301002 | 04 | 1240 | PV/ESS f< 1 | BOOL |  |  |  | X | X
AC alarm | 1001 | 4 | 301002 | 04 | 1250 | PV/ESS f< 2 | BOOL |  |  |  | X | X
AC alarm | 1001 | 5 | 301002 | 04 | 1260 | PV/ESS f< 3 | BOOL |  |  |  | X | X
AC alarm | 1001 | 6 | 301002 | 04 | 1270 | BB U> 1 | BOOL |  |  |  | X | X
AC alarm | 1001 | 7 | 301002 | 04 | 1280 | BB U> 2 | BOOL |  |  |  | X | X
AC alarm | 1001 | 8 | 301002 | 04 | 1290 | BB U> 3 | BOOL |  |  |  | X | X
AC alarm | 1001 | 9 | 301002 | 04 | 1300 | BB U< 1 | BOOL |  |  |  | X | X
AC alarm | 1001 | 10 | 301002 | 04 | 1310 | BB U< 2 | BOOL |  |  |  | X | X
AC alarm | 1001 | 11 | 301002 | 04 | 1320 | BB U< 3 | BOOL |  |  |  | X | X
AC alarm | 1001 | 12 | 301002 | 04 | 1330 | BB U< 4 | BOOL |  |  |  | X | X
AC alarm | 1001 | 13 | 301002 | 04 | 1350 | BB f> 1 | BOOL |  |  |  | X | X
AC alarm | 1001 | 14 | 301002 | 04 | 1360 | BB f> 2 | BOOL |  |  |  | X | X
AC alarm | 1001 | 15 | 301002 | 04 | 1370 | BB f> 3 | BOOL |  |  |  | X | X
AC alarm | 1002 | 0 | 301003 | 04 | 1380 | BB f< 1 | BOOL |  |  |  | X | X
AC alarm | 1002 | 1 | 301003 | 04 | 1390 | BB f< 2 | BOOL |  |  |  | X | X
AC alarm | 1002 | 2 | 301003 | 04 | 1400 | BB f< 3 | BOOL |  |  |  | X | X
AC alarm | 1002 | 3 | 301003 | 04 | 1410 | BB f< 4 | BOOL |  |  |  | X | X
AC alarm | 1002 | 7 | 301003 | 04 | 1450 | PV/ESS P> 1 | BOOL |  |  |  | X | X
AC alarm | 1002 | 8 | 301003 | 04 | 1460 | PV/ESS P> 2 | BOOL |  |  |  | X | X
AC alarm | 1002 | 9 | 301003 | 04 | 1470 | PV/ESS P> 3 | BOOL |  |  |  | X | X
AC alarm | 1002 | 10 | 301003 | 04 | 1480 | PV/ESS P> 4 | BOOL |  |  |  | X | X
AC alarm | 1002 | 11 | 301003 | 04 | 1490 | PV/ESS P> 5 | BOOL |  |  |  | X | X
AC alarm | 1004 | 8 | 301005 | 04 | 1981 | ESB ext. trip | BOOL |  |  |  |  | X
AC alarm | 1004 | 8 | 301005 | 04 | 1981 | PVB ext. trip | BOOL |  |  |  | X
AC alarm | 1004 | 10 | 301005 | 04 | 1650 | Ut< 1 monitoring active | BOOL |  |  |  | X | X
AC alarm | 1004 | 11 | 301005 | 04 | 1660 | Ut< 1 | BOOL |  |  |  | X | X
AC alarm | 1004 | 12 | 301005 | 04 | 1690 | Ut< 2 monitoring active | BOOL |  |  |  | X | X
AC alarm | 1004 | 13 | 301005 | 04 | 1700 | Ut< 2 | BOOL |  |  |  | X | X
AC alarm | 1004 | 14 | 301005 | 04 | 1760 | G P dep. Q< | BOOL |  |  |  | X | X
AC alarm | 1004 | 15 | 301005 | 04 | 1790 | G P dep. Q> | BOOL |  |  |  | X | X
Alarm | 1005 | 0 | 301006 | 04 | 2120 | Synchronising window | BOOL |  |  |  | X | X
Alarm | 1005 | 1 | 301006 | 04 | 2130 | Synchronising failure ESB | BOOL |  |  |  |  | X
Alarm | 1005 | 1 | 301006 | 04 | 2130 | Synchronising failure PVB | BOOL |  |  |  | X
AC alarm | 1005 | 3 | 301006 | 04 | 2150 | Phase seq error | BOOL |  |  |  | X | X
Alarm | 1005 | 4 | 301006 | 04 | 2160 | ESB open failure | BOOL |  |  |  |  | X
Alarm | 1005 | 4 | 301006 | 04 | 2160 | PVB open failure | BOOL |  |  |  | X
Alarm | 1005 | 5 | 301006 | 04 | 2170 | ESB close failure | BOOL |  |  |  |  | X
Alarm | 1005 | 5 | 301006 | 04 | 2170 | PVB close failure | BOOL |  |  |  | X
Alarm | 1005 | 6 | 301006 | 04 | 2180 | ESB pos. failure | BOOL |  |  |  |  | X
Alarm | 1005 | 6 | 301006 | 04 | 2180 | PVB pos. failure | BOOL |  |  |  | X
Alarm | 1007 | 0 | 301008 | 04 | 3000 | Digital alarm input 23 | BOOL |  |  |  | X | X
Alarm | 1007 | 1 | 301008 | 04 | 3010 | Digital alarm input 24 | BOOL |  |  |  | X | X
Alarm | 1007 | 2 | 301008 | 04 | 3020 | Digital alarm input 25 | BOOL |  |  |  | X | X
Alarm | 1007 | 3 | 301008 | 04 | 3030 | Digital alarm input 26 | BOOL |  |  |  | X | X
Alarm | 1007 | 4 | 301008 | 04 | 3040 | Digital alarm input 27 | BOOL |  |  |  | X | X
Alarm | 1007 | 6 | 301008 | 04 | 3060 | Digital alarm input 29 | BOOL |  |  |  | X | X
Alarm | 1007 | 7 | 301008 | 04 | 3070 | Digital alarm input 30 | BOOL |  |  |  | X | X
Alarm | 1007 | 8 | 301008 | 04 | 3080 | Digital alarm input 31 | BOOL |  |  |  | X | X
Alarm | 1007 | 9 | 301008 | 04 | 3090 | Digital alarm input 32 | BOOL |  |  |  | X | X
Alarm | 1007 | 10 | 301008 | 04 | 3100 | Digital alarm input 33 | BOOL |  |  |  | X | X
Alarm | 1007 | 11 | 301008 | 04 | 3110 | Digital alarm input 34 | BOOL |  |  |  | X | X
Alarm | 1007 | 12 | 301008 | 04 | 3120 | Digital alarm input 35 | BOOL |  |  |  | X | X
Alarm | 1008 | 0 | 301009 | 04 | 3130 | Digital alarm input 43 | BOOL |  |  |  | X | X
Alarm | 1008 | 1 | 301009 | 04 | 3140 | Digital alarm input 44 | BOOL |  |  |  | X | X
Alarm | 1008 | 2 | 301009 | 04 | 3150 | Digital alarm input 45 | BOOL |  |  |  | X | X
Alarm | 1008 | 3 | 301009 | 04 | 3160 | Digital alarm input 46 | BOOL |  |  |  | X | X
Alarm | 1008 | 4 | 301009 | 04 | 3170 | Digital alarm input 47 | BOOL |  |  |  | X | X
Alarm | 1008 | 5 | 301009 | 04 | 3180 | Digital alarm input 48 | BOOL |  |  |  | X | X
Alarm | 1008 | 6 | 301009 | 04 | 3190 | Digital alarm input 49 | BOOL |  |  |  | X | X
Alarm | 1008 | 7 | 301009 | 04 | 3200 | Digital alarm input 50 | BOOL |  |  |  | X | X
Alarm | 1008 | 8 | 301009 | 04 | 3210 | Digital alarm input 51 | BOOL |  |  |  | X | X
Alarm | 1008 | 9 | 301009 | 04 | 3220 | Digital alarm input 52 | BOOL |  |  |  | X | X
Alarm | 1008 | 10 | 301009 | 04 | 3230 | Digital alarm input 53 | BOOL |  |  |  | X | X
Alarm | 1008 | 11 | 301009 | 04 | 3240 | Digital alarm input 54 | BOOL |  |  |  | X | X
Alarm | 1008 | 12 | 301009 | 04 | 3250 | Digital alarm input 55 | BOOL |  |  |  | X | X
Alarm | 1009 | 0 | 301010 | 04 | 3260 | Digital alarm input 65 | BOOL |  |  |  | X | X
Alarm | 1009 | 1 | 301010 | 04 | 3270 | Digital alarm input 66 | BOOL |  |  |  | X | X
Alarm | 1009 | 2 | 301010 | 04 | 3280 | Digital alarm input 67 | BOOL |  |  |  | X | X
Alarm | 1009 | 3 | 301010 | 04 | 3290 | Digital alarm input 68 | BOOL |  |  |  | X | X
Alarm | 1009 | 4 | 301010 | 04 | 3300 | Digital alarm input 69 | BOOL |  |  |  | X | X
Alarm | 1009 | 5 | 301010 | 04 | 3310 | Digital alarm input 70 | BOOL |  |  |  | X | X
Alarm | 1009 | 6 | 301010 | 04 | 3320 | Digital alarm input 71 | BOOL |  |  |  | X | X
Alarm | 1009 | 7 | 301010 | 04 | 3330 | Digital alarm input 91 | BOOL |  |  |  | X | X
Alarm | 1009 | 8 | 301010 | 04 | 3340 | Digital alarm input 92 | BOOL |  |  |  | X | X
Alarm | 1009 | 9 | 301010 | 04 | 3350 | Digital alarm input 93 | BOOL |  |  |  | X | X
Alarm | 1009 | 10 | 301010 | 04 | 3360 | Digital alarm input 94 | BOOL |  |  |  | X | X
Alarm | 1009 | 11 | 301010 | 04 | 3370 | Digital alarm input 95 | BOOL |  |  |  | X | X
Alarm | 1009 | 12 | 301010 | 04 | 3380 | Digital alarm input 96 | BOOL |  |  |  | X | X
Alarm | 1009 | 13 | 301010 | 04 | 3390 | Digital alarm input 97 | BOOL |  |  |  | X | X
Alarm | 1010 | 0 | 301011 | 04 | 3400 | Multi-in. Alarm 102 | BOOL |  |  |  | X | X
Alarm | 1010 | 1 | 301011 | 04 | 3410 | Multi-in. Alarm 105 | BOOL |  |  |  | X | X
Alarm | 1010 | 2 | 301011 | 04 | 3420 | Multi-in. Alarm 108 | BOOL |  |  |  | X | X
Alarm | 1010 | 3 | 301011 | 04 | 3401 | Wire fail. 102 | BOOL |  |  |  | X | X
Alarm | 1010 | 4 | 301011 | 04 | 3411 | Wire fail. 105 | BOOL |  |  |  | X | X
Alarm | 1010 | 5 | 301011 | 04 | 3421 | Wire fail. 108 | BOOL |  |  |  | X | X
Alarm | 1010 | 6 | 301011 | 04 | 3430 | Digital alarm input 112 | BOOL |  |  |  | X | X
Alarm | 1010 | 7 | 301011 | 04 | 3440 | Digital alarm input 113 | BOOL |  |  |  | X | X
Alarm | 1010 | 8 | 301011 | 04 | 3450 | Digital alarm input 114 | BOOL |  |  |  | X | X
Alarm | 1010 | 9 | 301011 | 04 | 3460 | Digital alarm input 115 | BOOL |  |  |  | X | X
Alarm | 1010 | 10 | 301011 | 04 | 3470 | Digital alarm input 116 | BOOL |  |  |  | X | X
Alarm | 1010 | 11 | 301011 | 04 | 3480 | Digital alarm input 117 | BOOL |  |  |  | X | X
Alarm | 1011 | 0 | 301012 | 04 | 3500 | Digital alarm input 127 | BOOL |  |  |  | X | X
Alarm | 1011 | 1 | 301012 | 04 | 3510 | Digital alarm input 128 | BOOL |  |  |  | X | X
Alarm | 1011 | 2 | 301012 | 04 | 3520 | Digital alarm input 129 | BOOL |  |  |  | X | X
Alarm | 1011 | 3 | 301012 | 04 | 3530 | Digital alarm input 130 | BOOL |  |  |  | X | X
Alarm | 1011 | 4 | 301012 | 04 | 3540 | Digital alarm input 131 | BOOL |  |  |  | X | X
Alarm | 1011 | 5 | 301012 | 04 | 3550 | Digital alarm input 132 | BOOL |  |  |  | X | X
Alarm | 1011 | 6 | 301012 | 04 | 3560 | Digital alarm input 133 | BOOL |  |  |  | X | X
Alarm | 1011 | 7 | 301012 | 04 | 3570 | M-Logic alarm 1 | BOOL |  |  |  | X | X
Alarm | 1011 | 8 | 301012 | 04 | 3580 | M-Logic alarm 2 | BOOL |  |  |  | X | X
Alarm | 1011 | 9 | 301012 | 04 | 3590 | M-Logic alarm 3 | BOOL |  |  |  | X | X
Alarm | 1011 | 10 | 301012 | 04 | 3600 | M-Logic alarm 4 | BOOL |  |  |  | X | X
Alarm | 1011 | 11 | 301012 | 04 | 3610 | M-Logic alarm 5 | BOOL |  |  |  | X | X
Alarm | 1012 | 0 | 301013 | 04 | 4000 | Analogue input 91.1 | BOOL |  |  |  | X | X
Alarm | 1012 | 1 | 301013 | 04 | 4010 | Analogue input 91.2 | BOOL |  |  |  | X | X
Alarm | 1012 | 2 | 301013 | 04 | 4020 | Wire failure analogue 91 | BOOL |  |  |  | X | X
Alarm | 1012 | 3 | 301013 | 04 | 4030 | Analogue input 93.1 | BOOL |  |  |  | X | X
Alarm | 1012 | 4 | 301013 | 04 | 4040 | Analogue input 93.2 | BOOL |  |  |  | X | X
Alarm | 1012 | 5 | 301013 | 04 | 4050 | Wire failure analogue 93 | BOOL |  |  |  | X | X
Alarm | 1012 | 6 | 301013 | 04 | 4060 | Analogue input 95.1 | BOOL |  |  |  | X | X
Alarm | 1012 | 7 | 301013 | 04 | 4070 | Analogue input 95.2 | BOOL |  |  |  | X | X
Alarm | 1012 | 8 | 301013 | 04 | 4080 | Wire failure analogue 95 | BOOL |  |  |  | X | X
Alarm | 1012 | 9 | 301013 | 04 | 4090 | Analogue input 97.1 | BOOL |  |  |  | X | X
Alarm | 1012 | 10 | 301013 | 04 | 4100 | Analogue input 97.2 | BOOL |  |  |  | X | X
Alarm | 1012 | 11 | 301013 | 04 | 4110 | Wire failure analogue 97 | BOOL |  |  |  | X | X
Alarm | 1013 | 0 | 301014 | 04 | 4120, 4140, 4160, 4180, 4200, 4220 | Multi input terminal 102.1 | BOOL |  |  |  | X | X
Alarm | 1013 | 1 | 301014 | 04 | 4130, 4150, 4170, 4190, 4210, 4230 | Multi input terminal 102.2 | BOOL |  |  |  | X | X
Alarm | 1013 | 2 | 301014 | 04 | 4240 | W. fail. 102 | BOOL |  |  |  | X | X
Alarm | 1013 | 3 | 301014 | 04 | 4250, 4270, 4290, 4310, 4330, 4350 | Multi input terminal 105.1 | BOOL |  |  |  | X | X
Alarm | 1013 | 4 | 301014 | 04 | 4260, 4280, 4300, 4320, 4340, 4360 | Multi input terminal 105.2 | BOOL |  |  |  | X | X
Alarm | 1013 | 5 | 301014 | 04 | 4370 | W. fail. 105 | BOOL |  |  |  | X | X
Alarm | 1013 | 6 | 301014 | 04 | 4380, 4400, 4420, 4440, 4460, 4480 | Multi input terminal 108.1 | BOOL |  |  |  | X | X
Alarm | 1013 | 7 | 301014 | 04 | 4390, 4410, 4430, 4450, 4470, 4490 | Multi input terminal 108.2 | BOOL |  |  |  | X | X
Alarm | 1014 | 1 | 301015 | 04 | 4960 | U< aux. term. 1 | BOOL |  |  |  | X | X
Alarm | 1014 | 2 | 301015 | 04 | 4970 | U> aux. term. 1 | BOOL |  |  |  | X | X
Alarm | 1014 | 3 | 301015 | 04 | 4980 | U< aux. term. 98 | BOOL |  |  |  | X | X
Alarm | 1014 | 4 | 301015 | 04 | 4990 | U> aux. term. 98 | BOOL |  |  |  | X | X
Alarm | 1015 | 3 | 301016 | 04 | 6280 | Internal communication failure | BOOL |  |  |  | X | X
Alarm | 1015 | 12 | 301016 | 04 | 6540 | Unit not in auto | BOOL |  |  |  | X | X
Relay state | 1016 | 0 | 301017 | 04 | 5000 | Relay 5 | BOOL |  |  |  | X | X
Relay state | 1016 | 1 | 301017 | 04 | 5010 | Relay 8 | BOOL |  |  |  | X | X
Relay state | 1016 | 2 | 301017 | 04 | 5020 | Relay 11 | BOOL |  |  |  | X | X
Relay state | 1016 | 3 | 301017 | 04 | 5030 | Relay 14 | BOOL |  |  |  | X | X
Relay state | 1016 | 4 | 301017 | 04 | 5040 | Relay 17 | BOOL |  |  |  | X | X
Relay state | 1016 | 5 | 301017 | 04 | 5050 | Relay 20 | BOOL |  |  |  | X | X
Relay state | 1016 | 6 | 301017 | 04 | 5060 | Relay 21 | BOOL |  |  |  | X | X
Relay state | 1016 | 7 | 301017 | 04 | 5070 | Relay 29 | BOOL |  |  |  | X | X
Relay state | 1016 | 8 | 301017 | 04 | 5080 | Relay 31 | BOOL |  |  |  | X | X
Relay state | 1016 | 9 | 301017 | 04 | 5090 | Relay 33 | BOOL |  |  |  | X | X
Relay state | 1016 | 10 | 301017 | 04 | 5100 | Relay 35 | BOOL |  |  |  | X | X
Relay state | 1016 | 11 | 301017 | 04 | 5110 | Relay 57 | BOOL |  |  |  | X | X
Relay state | 1016 | 12 | 301017 | 04 | 5120 | Relay 59 | BOOL |  |  |  | X | X
Relay state | 1016 | 13 | 301017 | 04 | 5130 | Relay 61 | BOOL |  |  |  | X | X
Relay state | 1016 | 14 | 301017 | 04 | 5140 | Relay 63 | BOOL |  |  |  | X | X
Relay state | 1017 | 0 | 301018 | 04 | 5150 | Relay 65 | BOOL |  |  |  | X | X
Relay state | 1017 | 1 | 301018 | 04 | 5160 | Relay 67 | BOOL |  |  |  | X | X
Relay state | 1017 | 2 | 301018 | 04 | 5170 | Relay 69 | BOOL |  |  |  | X | X
Relay state | 1017 | 3 | 301018 | 04 | 5180 | Relay 71 | BOOL |  |  |  | X | X
Relay state | 1017 | 4 | 301018 | 04 | 5190 | Relay 90 | BOOL |  |  |  | X | X
Relay state | 1017 | 5 | 301018 | 04 | 5200 | Relay 92 | BOOL |  |  |  | X | X
Relay state | 1017 | 6 | 301018 | 04 | 5210 | Relay 94 | BOOL |  |  |  | X | X
Relay state | 1017 | 7 | 301018 | 04 | 5220 | Relay 96 | BOOL |  |  |  | X | X
Relay state | 1017 | 8 | 301018 | 04 | 5230 | Relay 126 | BOOL |  |  |  | X | X
Relay state | 1017 | 9 | 301018 | 04 | 5240 | Relay 128 | BOOL |  |  |  | X | X
Relay state | 1017 | 10 | 301018 | 04 | 5250 | Relay 130 | BOOL |  |  |  | X | X
Relay state | 1017 | 11 | 301018 | 04 | 5260 | Relay 132 | BOOL |  |  |  | X | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | ESB position ON | BOOL |  |  |  |  | X
Plant logic state | 1018 | 4 | 301019 | 04 |  | PVB position ON | BOOL |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | ESB synchronising | BOOL |  |  |  |  | X
Plant logic state | 1018 | 5 | 301019 | 04 |  | PVB synchronising | BOOL |  |  |  | X
Plant logic state | 1018 | 6 | 301019 | 04 |  | PV running | BOOL |  |  |  | X
Plant logic state | 1018 | 8 | 301019 | 04 | 6220 | Hz/V OK, timer expired | BOOL |  |  |  | X | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | ESB position OFF | BOOL |  |  |  |  | X
Plant logic state | 1018 | 11 | 301019 | 04 |  | PVB position OFF | BOOL |  |  |  | X
Plant logic state | 1018 | 13 | 301019 | 04 |  | BB Hz/V OK | BOOL |  |  |  | X | X
Modes | 1019 | 2 | 301020 | 04 |  | Semi auto mode | BOOL |  |  |  | X | X
Modes | 1019 | 3 | 301020 | 04 |  | Auto mode | BOOL |  |  |  | X | X
Modes | 1019 | 5 | 301020 | 04 |  | Island | BOOL |  |  |  | X | X
Modes | 1019 | 7 | 301020 | 04 |  | Peak shaving | BOOL |  |  |  | X | X
Modes | 1019 | 8 | 301020 | 04 |  | Fixed power | BOOL |  |  |  | X | X
Modes | 1019 | 9 | 301020 | 04 |  | Mains power export | BOOL |  |  |  | X | X
Modes | 1019 | 11 | 301020 | 04 |  | Power management | BOOL |  |  |  | X | X
PM alarm | 1031 | 1 | 301032 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X
PM alarm | 1031 | 2 | 301032 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X
PM alarm | 1031 | 3 | 301032 | 04 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X
PM alarm | 1031 | 4 | 301032 | 04 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X
PM alarm | 1031 | 5 | 301032 | 04 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X
PM alarm | 1031 | 6 | 301032 | 04 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X
PM alarm | 1031 | 7 | 301032 | 04 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X
PM alarm | 1031 | 8 | 301032 | 04 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X
PM alarm | 1031 | 9 | 301032 | 04 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X
PM alarm | 1031 | 10 | 301032 | 04 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X
PM alarm | 1031 | 11 | 301032 | 04 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X
PM alarm | 1031 | 12 | 301032 | 04 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X
PM alarm | 1031 | 13 | 301032 | 04 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X
PM alarm | 1031 | 14 | 301032 | 04 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X
PM alarm | 1031 | 15 | 301032 | 04 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X
PM alarm | 1032 | 0 | 301033 | 04 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X
PM alarm | 1032 | 2 | 301033 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X
PM alarm | 1032 | 3 | 301033 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X
PM alarm | 1032 | 4 | 301033 | 04 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X
PM alarm | 1032 | 5 | 301033 | 04 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X
PM alarm | 1032 | 6 | 301033 | 04 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X
PM alarm | 1032 | 7 | 301033 | 04 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X
PM alarm | 1032 | 8 | 301033 | 04 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X
PM alarm | 1032 | 9 | 301033 | 04 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X
PM alarm | 1032 | 10 | 301033 | 04 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X
PM alarm | 1032 | 11 | 301033 | 04 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X
PM alarm | 1032 | 12 | 301033 | 04 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X
PM alarm | 1032 | 13 | 301033 | 04 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X
PM alarm | 1032 | 14 | 301033 | 04 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X
PM alarm | 1032 | 15 | 301033 | 04 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X
PM alarm | 1033 | 0 | 301034 | 04 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X
PM alarm | 1033 | 1 | 301034 | 04 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X
Alarm | 1033 | 2 | 301034 | 04 | 7520 | Communication error ext. | BOOL |  |  |  | X | X
PM alarm | 1034 | 1 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 1 | BOOL |  |  |  | X | X
PM alarm | 1034 | 2 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 2 | BOOL |  |  |  | X | X
PM alarm | 1034 | 3 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 3 | BOOL |  |  |  | X | X
PM alarm | 1034 | 4 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 4 | BOOL |  |  |  | X | X
PM alarm | 1034 | 5 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 5 | BOOL |  |  |  | X | X
PM alarm | 1034 | 6 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 6 | BOOL |  |  |  | X | X
PM alarm | 1034 | 7 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 7 | BOOL |  |  |  | X | X
PM alarm | 1034 | 8 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 8 | BOOL |  |  |  | X | X
PM alarm | 1034 | 9 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 9 | BOOL |  |  |  | X | X
PM alarm | 1034 | 10 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 10 | BOOL |  |  |  | X | X
PM alarm | 1034 | 11 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 11 | BOOL |  |  |  | X | X
PM alarm | 1034 | 12 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 12 | BOOL |  |  |  | X | X
PM alarm | 1034 | 13 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 13 | BOOL |  |  |  | X | X
PM alarm | 1034 | 14 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 14 | BOOL |  |  |  | X | X
PM alarm | 1034 | 15 | 301035 | 04 |  | Ext. Modbus comm. error, CAN ID 15 | BOOL |  |  |  | X | X
PM alarm | 1035 | 0 | 301036 | 04 |  | Ext. Modbus comm. error, CAN ID 16 | BOOL |  |  |  | X | X
PM alarm | 1040 | 0 | 301041 | 04 |  | CAN 1 missing ID 1 | BOOL |  |  |  | X | X
PM alarm | 1040 | 1 | 301041 | 04 |  | CAN 1 missing ID 2 | BOOL |  |  |  | X | X
PM alarm | 1040 | 2 | 301041 | 04 |  | CAN 1 missing ID 3 | BOOL |  |  |  | X | X
PM alarm | 1040 | 3 | 301041 | 04 |  | CAN 1 missing ID 4 | BOOL |  |  |  | X | X
PM alarm | 1040 | 4 | 301041 | 04 |  | CAN 1 missing ID 5 | BOOL |  |  |  | X | X
PM alarm | 1040 | 5 | 301041 | 04 |  | CAN 1 missing ID 6 | BOOL |  |  |  | X | X
PM alarm | 1040 | 6 | 301041 | 04 |  | CAN 1 missing ID 7 | BOOL |  |  |  | X | X
PM alarm | 1040 | 7 | 301041 | 04 |  | CAN 1 missing ID 8 | BOOL |  |  |  | X | X
PM alarm | 1040 | 8 | 301041 | 04 |  | CAN 1 missing ID 9 | BOOL |  |  |  | X | X
PM alarm | 1040 | 9 | 301041 | 04 |  | CAN 1 missing ID 10 | BOOL |  |  |  | X | X
PM alarm | 1040 | 10 | 301041 | 04 |  | CAN 1 missing ID 11 | BOOL |  |  |  | X | X
PM alarm | 1040 | 11 | 301041 | 04 |  | CAN 1 missing ID 12 | BOOL |  |  |  | X | X
PM alarm | 1040 | 12 | 301041 | 04 |  | CAN 1 missing ID 13 | BOOL |  |  |  | X | X
PM alarm | 1040 | 13 | 301041 | 04 |  | CAN 1 missing ID 14 | BOOL |  |  |  | X | X
PM alarm | 1040 | 14 | 301041 | 04 |  | CAN 1 missing ID 15 | BOOL |  |  |  | X | X
PM alarm | 1040 | 15 | 301041 | 04 |  | CAN 1 missing ID 16 | BOOL |  |  |  | X | X
PM alarm | 1041 | 0 | 301042 | 04 |  | CAN 1 missing ID 17 | BOOL |  |  |  | X | X
PM alarm | 1041 | 1 | 301042 | 04 |  | CAN 1 missing ID 18 | BOOL |  |  |  | X | X
PM alarm | 1041 | 2 | 301042 | 04 |  | CAN 1 missing ID 19 | BOOL |  |  |  | X | X
PM alarm | 1041 | 3 | 301042 | 04 |  | CAN 1 missing ID 20 | BOOL |  |  |  | X | X
PM alarm | 1041 | 4 | 301042 | 04 |  | CAN 1 missing ID 21 | BOOL |  |  |  | X | X
PM alarm | 1041 | 5 | 301042 | 04 |  | CAN 1 missing ID 22 | BOOL |  |  |  | X | X
PM alarm | 1041 | 6 | 301042 | 04 |  | CAN 1 missing ID 23 | BOOL |  |  |  | X | X
PM alarm | 1041 | 7 | 301042 | 04 |  | CAN 1 missing ID 24 | BOOL |  |  |  | X | X
PM alarm | 1041 | 8 | 301042 | 04 |  | CAN 1 missing ID 25 | BOOL |  |  |  | X | X
PM alarm | 1041 | 9 | 301042 | 04 |  | CAN 1 missing ID 26 | BOOL |  |  |  | X | X
PM alarm | 1041 | 10 | 301042 | 04 |  | CAN 1 missing ID 27 | BOOL |  |  |  | X | X
PM alarm | 1041 | 11 | 301042 | 04 |  | CAN 1 missing ID 28 | BOOL |  |  |  | X | X
PM alarm | 1041 | 12 | 301042 | 04 |  | CAN 1 missing ID 29 | BOOL |  |  |  | X | X
PM alarm | 1041 | 13 | 301042 | 04 |  | CAN 1 missing ID 30 | BOOL |  |  |  | X | X
PM alarm | 1041 | 14 | 301042 | 04 |  | CAN 1 missing ID 31 | BOOL |  |  |  | X | X
PM alarm | 1041 | 15 | 301042 | 04 |  | CAN 1 missing ID 32 | BOOL |  |  |  | X | X
PM alarm | 1042 | 0 | 301043 | 04 |  | CAN 1 missing ID 33 | BOOL |  |  |  | X | X
PM alarm | 1042 | 1 | 301043 | 04 |  | CAN 1 missing ID 34 | BOOL |  |  |  | X | X
PM alarm | 1042 | 2 | 301043 | 04 |  | CAN 1 missing ID 35 | BOOL |  |  |  | X | X
PM alarm | 1042 | 3 | 301043 | 04 |  | CAN 1 missing ID 36 | BOOL |  |  |  | X | X
PM alarm | 1042 | 4 | 301043 | 04 |  | CAN 1 missing ID 37 | BOOL |  |  |  | X | X
PM alarm | 1042 | 5 | 301043 | 04 |  | CAN 1 missing ID 38 | BOOL |  |  |  | X | X
PM alarm | 1042 | 6 | 301043 | 04 |  | CAN 1 missing ID 39 | BOOL |  |  |  | X | X
PM alarm | 1042 | 7 | 301043 | 04 |  | CAN 1 missing ID 40 | BOOL |  |  |  | X | X
PM alarm | 1043 | 0 | 301044 | 04 |  | CAN 2 missing ID 1 | BOOL |  |  |  | X | X
PM alarm | 1043 | 1 | 301044 | 04 |  | CAN 2 missing ID 2 | BOOL |  |  |  | X | X
PM alarm | 1043 | 2 | 301044 | 04 |  | CAN 2 missing ID 3 | BOOL |  |  |  | X | X
PM alarm | 1043 | 3 | 301044 | 04 |  | CAN 2 missing ID 4 | BOOL |  |  |  | X | X
PM alarm | 1043 | 4 | 301044 | 04 |  | CAN 2 missing ID 5 | BOOL |  |  |  | X | X
PM alarm | 1043 | 5 | 301044 | 04 |  | CAN 2 missing ID 6 | BOOL |  |  |  | X | X
PM alarm | 1043 | 6 | 301044 | 04 |  | CAN 2 missing ID 7 | BOOL |  |  |  | X | X
PM alarm | 1043 | 7 | 301044 | 04 |  | CAN 2 missing ID 8 | BOOL |  |  |  | X | X
PM alarm | 1043 | 8 | 301044 | 04 |  | CAN 2 missing ID 9 | BOOL |  |  |  | X | X
PM alarm | 1043 | 9 | 301044 | 04 |  | CAN 2 missing ID 10 | BOOL |  |  |  | X | X
PM alarm | 1043 | 10 | 301044 | 04 |  | CAN 2 missing ID 11 | BOOL |  |  |  | X | X
PM alarm | 1043 | 11 | 301044 | 04 |  | CAN 2 missing ID 12 | BOOL |  |  |  | X | X
PM alarm | 1043 | 12 | 301044 | 04 |  | CAN 2 missing ID 13 | BOOL |  |  |  | X | X
PM alarm | 1043 | 13 | 301044 | 04 |  | CAN 2 missing ID 14 | BOOL |  |  |  | X | X
PM alarm | 1043 | 14 | 301044 | 04 |  | CAN 2 missing ID 15 | BOOL |  |  |  | X | X
PM alarm | 1043 | 15 | 301044 | 04 |  | CAN 2 missing ID 16 | BOOL |  |  |  | X | X
PM alarm | 1044 | 0 | 301045 | 04 |  | CAN 2 missing ID 17 | BOOL |  |  |  | X | X
PM alarm | 1044 | 1 | 301045 | 04 |  | CAN 2 missing ID 18 | BOOL |  |  |  | X | X
PM alarm | 1044 | 2 | 301045 | 04 |  | CAN 2 missing ID 19 | BOOL |  |  |  | X | X
PM alarm | 1044 | 3 | 301045 | 04 |  | CAN 2 missing ID 20 | BOOL |  |  |  | X | X
PM alarm | 1044 | 4 | 301045 | 04 |  | CAN 2 missing ID 21 | BOOL |  |  |  | X | X
PM alarm | 1044 | 5 | 301045 | 04 |  | CAN 2 missing ID 22 | BOOL |  |  |  | X | X
PM alarm | 1044 | 6 | 301045 | 04 |  | CAN 2 missing ID 23 | BOOL |  |  |  | X | X
PM alarm | 1044 | 7 | 301045 | 04 |  | CAN 2 missing ID 24 | BOOL |  |  |  | X | X
PM alarm | 1044 | 8 | 301045 | 04 |  | CAN 2 missing ID 25 | BOOL |  |  |  | X | X
PM alarm | 1044 | 9 | 301045 | 04 |  | CAN 2 missing ID 26 | BOOL |  |  |  | X | X
PM alarm | 1044 | 10 | 301045 | 04 |  | CAN 2 missing ID 27 | BOOL |  |  |  | X | X
PM alarm | 1044 | 11 | 301045 | 04 |  | CAN 2 missing ID 28 | BOOL |  |  |  | X | X
PM alarm | 1044 | 12 | 301045 | 04 |  | CAN 2 missing ID 29 | BOOL |  |  |  | X | X
PM alarm | 1044 | 13 | 301045 | 04 |  | CAN 2 missing ID 30 | BOOL |  |  |  | X | X
PM alarm | 1044 | 14 | 301045 | 04 |  | CAN 2 missing ID 31 | BOOL |  |  |  | X | X
PM alarm | 1044 | 15 | 301045 | 04 |  | CAN 2 missing ID 32 | BOOL |  |  |  | X | X
PM alarm | 1045 | 0 | 301046 | 04 |  | CAN 2 missing ID 33 | BOOL |  |  |  | X | X
PM alarm | 1045 | 1 | 301046 | 04 |  | CAN 2 missing ID 34 | BOOL |  |  |  | X | X
PM alarm | 1045 | 2 | 301046 | 04 |  | CAN 2 missing ID 35 | BOOL |  |  |  | X | X
PM alarm | 1045 | 3 | 301046 | 04 |  | CAN 2 missing ID 36 | BOOL |  |  |  | X | X
PM alarm | 1045 | 4 | 301046 | 04 |  | CAN 2 missing ID 37 | BOOL |  |  |  | X | X
PM alarm | 1045 | 5 | 301046 | 04 |  | CAN 2 missing ID 38 | BOOL |  |  |  | X | X
PM alarm | 1045 | 6 | 301046 | 04 |  | CAN 2 missing ID 39 | BOOL |  |  |  | X | X
PM alarm | 1045 | 7 | 301046 | 04 |  | CAN 2 missing ID 40 | BOOL |  |  |  | X | X
Alarm | 1046 | 0 | 301047 | 04 | 4800 | Analogue input 127.1 | BOOL |  |  |  | X | X
Alarm | 1046 | 1 | 301047 | 04 | 4810 | Analogue input 127.2 | BOOL |  |  |  | X | X
Alarm | 1046 | 2 | 301047 | 04 | 4820 | Wire fail analogue input 127 | BOOL |  |  |  | X | X
Alarm | 1046 | 3 | 301047 | 04 | 4830 | Analogue input 129.1 | BOOL |  |  |  | X | X
Alarm | 1046 | 4 | 301047 | 04 | 4840 | Analogue input 129.2 | BOOL |  |  |  | X | X
Alarm | 1046 | 5 | 301047 | 04 | 4850 | Wire fail analogue input 129 | BOOL |  |  |  | X | X
Alarm | 1046 | 6 | 301047 | 04 | 4860 | Analogue input 131.1 | BOOL |  |  |  | X | X
Alarm | 1046 | 7 | 301047 | 04 | 4870 | Analogue input 131.2 | BOOL |  |  |  | X | X
Alarm | 1046 | 8 | 301047 | 04 | 4880 | Wire fail analogue input 131 | BOOL |  |  |  | X | X
Alarm | 1046 | 9 | 301047 | 04 | 4890 | Analogue input 133.1 | BOOL |  |  |  | X | X
Alarm | 1046 | 10 | 301047 | 04 | 4900 | Analogue input 133.2 | BOOL |  |  |  | X | X
Alarm | 1046 | 11 | 301047 | 04 | 4910 | Wire fail analogue input 133 | BOOL |  |  |  | X | X
Plant logic state | 1050 | 0 | 301051 | 04 |  | Ready to autostart | BOOL |  |  |  | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | ESB U > 30% of U nominal | BOOL |  |  |  |  | X
Plant logic state | 1050 | 1 | 301051 | 04 |  | PV U > 30% of U nominal | BOOL |  |  |  | X
Plant logic state | 1050 | 2 | 301051 | 04 |  | BB U > 30% of U nominal | BOOL |  |  |  | X | X
M-Logic state | 1051 |  | 301052 | 04 |  | Virtual events 1-16 | INT16s | AB | 0 |  | X | X
M-Logic state | 1052 |  | 301053 | 04 |  | Virtual events 17-32 | INT16s | AB | 0 |  | X | X
Alarm | 1053 | 4 | 301054 | 04 | 4610 | Delta analogue 1 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 5 | 301054 | 04 | 4620 | Delta analogue 1 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 6 | 301054 | 04 | 4630 | Delta analogue 2 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 7 | 301054 | 04 | 4640 | Delta analogue 2 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 8 | 301054 | 04 | 4650 | Delta analogue 3 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 9 | 301054 | 04 | 4660 | Delta analogue 3 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 10 | 301054 | 04 | 4680 | Delta analogue 4 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 11 | 301054 | 04 | 4690 | Delta analogue 4 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 12 | 301054 | 04 | 4700 | Delta analogue 5 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 13 | 301054 | 04 | 4710 | Delta analogue 5 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1053 | 14 | 301054 | 04 | 4720 | Delta analogue 6 - fail 1 | BOOL |  |  |  | X | X
Alarm | 1053 | 15 | 301054 | 04 | 4730 | Delta analogue 6 - fail 2 | BOOL |  |  |  | X | X
Alarm | 1057 | 1 | 301058 | 04 |  | Fail class: Warning | BOOL |  |  |  | X | X
Alarm | 1057 | 2 | 301058 | 04 |  | Fail class: Shutdown | BOOL |  |  |  | X | X
Plant logic state | 1058 |  | 301059 | 04 |  | Flipflop output 1-16 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1500 |  | 301501 | 04 |  | Total power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1501 |  | 301502 | 04 |  | Available power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1502 |  | 301503 | 04 |  | Total nominal power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1503 |  | 301504 | 04 |  | Total active power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1504 |  | 301505 | 04 |  | Total reactive power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1505 |  | 301506 | 04 |  | Number of gensets in application | INT16s | AB | 0 |  | X | X
PM AC measurement | 1506 |  | 301507 | 04 |  | Plant type | INT16s | AB | 0 |  | X | X
PM AC measurement | 1507 |  | 301508 | 04 |  | Load-dependent stop, active set-point | INT16s | AB | 0 |  | X | X
PM AC measurement | 1508 |  | 301509 | 04 |  | Load-dependent start, active set-point | INT16s | AB | 0 |  | X | X
PM AC measurement | 1510 |  | 301511 | 04 |  | Nominal power ID 1 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1511 |  | 301512 | 04 |  | Nominal power ID 2 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1512 |  | 301513 | 04 |  | Nominal power ID 3 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1513 |  | 301514 | 04 |  | Nominal power ID 4 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1514 |  | 301515 | 04 |  | Nominal power ID 5 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1515 |  | 301516 | 04 |  | Nominal power ID 6 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1516 |  | 301517 | 04 |  | Nominal power ID 7 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1517 |  | 301518 | 04 |  | Nominal power ID 8 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1518 |  | 301519 | 04 |  | Nominal power ID 9 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1519 |  | 301520 | 04 |  | Nominal power ID 10 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1520 |  | 301521 | 04 |  | Nominal power ID 11 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1521 |  | 301522 | 04 |  | Nominal power ID 12 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1522 |  | 301523 | 04 |  | Nominal power ID 13 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1523 |  | 301524 | 04 |  | Nominal power ID 14 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1524 |  | 301525 | 04 |  | Nominal power ID 15 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1525 |  | 301526 | 04 |  | Nominal power ID 16 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1526 |  | 301527 | 04 |  | Active Power ID 1 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1527 |  | 301528 | 04 |  | Active Power ID 2 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1528 |  | 301529 | 04 |  | Active Power ID 3 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1529 |  | 301530 | 04 |  | Active Power ID 4 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1530 |  | 301531 | 04 |  | Active Power ID 5 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1531 |  | 301532 | 04 |  | Active Power ID 6 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1532 |  | 301533 | 04 |  | Active Power ID 7 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1533 |  | 301534 | 04 |  | Active Power ID 8 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1534 |  | 301535 | 04 |  | Active Power ID 9 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1535 |  | 301536 | 04 |  | Active Power ID 10 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1536 |  | 301537 | 04 |  | Active Power ID 11 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1537 |  | 301538 | 04 |  | Active Power ID 12 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1538 |  | 301539 | 04 |  | Active Power ID 13 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1539 |  | 301540 | 04 |  | Active Power ID 14 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1540 |  | 301541 | 04 |  | Active Power ID 15 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1541 |  | 301542 | 04 |  | Active Power ID 16 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1542 |  | 301543 | 04 |  | Reactive Power ID 1 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1543 |  | 301544 | 04 |  | Reactive Power ID 2 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1544 |  | 301545 | 04 |  | Reactive Power ID 3 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1545 |  | 301546 | 04 |  | Reactive Power ID 4 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1546 |  | 301547 | 04 |  | Reactive Power ID 5 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1547 |  | 301548 | 04 |  | Reactive Power ID 6 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1548 |  | 301549 | 04 |  | Reactive Power ID 7 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1549 |  | 301550 | 04 |  | Reactive Power ID 8 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1550 |  | 301551 | 04 |  | Reactive Power ID 9 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1551 |  | 301552 | 04 |  | Reactive Power ID 10 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1552 |  | 301553 | 04 |  | Reactive Power ID 11 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1553 |  | 301554 | 04 |  | Reactive Power ID 12 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1554 |  | 301555 | 04 |  | Reactive Power ID 13 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1555 |  | 301556 | 04 |  | Reactive Power ID 14 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1556 |  | 301557 | 04 |  | Reactive Power ID 15 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1557 |  | 301558 | 04 |  | Reactive Power ID 16 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1560 |  | 301561 | 04 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1561 |  | 301562 | 04 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1562 |  | 301563 | 04 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1563 |  | 301564 | 04 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1565 |  | 301566 | 04 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1566 |  | 301567 | 04 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1567 |  | 301568 | 04 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1568 |  | 301569 | 04 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1569 |  | 301570 | 04 |  | Active Power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1570 |  | 301571 | 04 |  | Active Power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1571 |  | 301572 | 04 |  | Active Power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1572 |  | 301573 | 04 |  | Active Power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1573 |  | 301574 | 04 |  | Active Power ID 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1574 |  | 301575 | 04 |  | Active Power ID 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1575 |  | 301576 | 04 |  | Active Power ID 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1576 |  | 301577 | 04 |  | Active Power ID 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1577 |  | 301578 | 04 |  | Active Power ID 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1578 |  | 301579 | 04 |  | Active Power ID 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1579 |  | 301580 | 04 |  | Active Power ID 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1580 |  | 301581 | 04 |  | Active Power ID 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1581 |  | 301582 | 04 |  | Active Power ID 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1582 |  | 301583 | 04 |  | Active Power ID 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1583 |  | 301584 | 04 |  | Active Power ID 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1584 |  | 301585 | 04 |  | Active Power ID 32 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1585 |  | 301586 | 04 |  | Reactive Power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1586 |  | 301587 | 04 |  | Reactive Power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1587 |  | 301588 | 04 |  | Reactive Power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1588 |  | 301589 | 04 |  | Reactive Power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1589 |  | 301590 | 04 |  | Reactive Power ID 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1590 |  | 301591 | 04 |  | Reactive Power ID 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1591 |  | 301592 | 04 |  | Reactive Power ID 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1592 |  | 301593 | 04 |  | Reactive Power ID 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1593 |  | 301594 | 04 |  | Reactive Power ID 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1594 |  | 301595 | 04 |  | Reactive Power ID 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1595 |  | 301596 | 04 |  | Reactive Power ID 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1596 |  | 301597 | 04 |  | Reactive Power ID 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1597 |  | 301598 | 04 |  | Reactive Power ID 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1598 |  | 301599 | 04 |  | Reactive Power ID 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1599 |  | 301600 | 04 |  | Reactive Power ID 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1600 |  | 301601 | 04 |  | Reactive Power ID 32 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1601 |  | 301602 | 04 |  | Active Power ID 33 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1602 |  | 301603 | 04 |  | Active Power ID 34 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1603 |  | 301604 | 04 |  | Active Power ID 35 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1604 |  | 301605 | 04 |  | Active Power ID 36 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1605 |  | 301606 | 04 |  | Active Power ID 37 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1606 |  | 301607 | 04 |  | Active Power ID 38 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1607 |  | 301608 | 04 |  | Active Power ID 39 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1608 |  | 301609 | 04 |  | Active Power ID 40 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1609 |  | 301610 | 04 |  | Reactive Power ID 33 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1610 |  | 301611 | 04 |  | Reactive Power ID 34 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1611 |  | 301612 | 04 |  | Reactive Power ID 35 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1612 |  | 301613 | 04 |  | Reactive Power ID 36 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1613 |  | 301614 | 04 |  | Reactive Power ID 37 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1614 |  | 301615 | 04 |  | Reactive Power ID 38 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1615 |  | 301616 | 04 |  | Reactive Power ID 39 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1616 |  | 301617 | 04 |  | Reactive Power ID 40 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1617 |  | 301618 | 04 |  | Plant mode mains 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1618 |  | 301619 | 04 |  | Plant mode mains 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1619 |  | 301620 | 04 |  | Plant mode mains 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1620 |  | 301621 | 04 |  | Plant mode mains 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1621 |  | 301622 | 04 |  | Plant mode mains 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1622 |  | 301623 | 04 |  | Plant mode mains 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1623 |  | 301624 | 04 |  | Plant mode mains 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1624 |  | 301625 | 04 |  | Plant mode mains 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1625 |  | 301626 | 04 |  | Plant mode mains 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1626 |  | 301627 | 04 |  | Plant mode mains 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1627 |  | 301628 | 04 |  | Plant mode mains 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1628 |  | 301629 | 04 |  | Plant mode mains 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1629 |  | 301630 | 04 |  | Plant mode mains 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1630 |  | 301631 | 04 |  | Plant mode mains 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1631 |  | 301632 | 04 |  | Plant mode mains 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1632 |  | 301633 | 04 |  | Plant mode mains 32 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1633 |  | 301634 | 04 |  | Bus power mains 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1634 |  | 301635 | 04 |  | Bus power mains 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1635 |  | 301636 | 04 |  | Bus power mains 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1636 |  | 301637 | 04 |  | Bus power mains 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1637 |  | 301638 | 04 |  | Bus power mains 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1638 |  | 301639 | 04 |  | Bus power mains 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1639 |  | 301640 | 04 |  | Bus power mains 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1640 |  | 301641 | 04 |  | Bus power mains 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1641 |  | 301642 | 04 |  | Bus power mains 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1642 |  | 301643 | 04 |  | Bus power mains 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1643 |  | 301644 | 04 |  | Bus power mains 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1644 |  | 301645 | 04 |  | Bus power mains 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1645 |  | 301646 | 04 |  | Bus power mains 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1646 |  | 301647 | 04 |  | Bus power mains 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1647 |  | 301648 | 04 |  | Bus power mains 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1648 |  | 301649 | 04 |  | Bus power mains 32 | INT16s | AB | 0 |  | X | X
PM Plant logic state | 1649 | 0 | 301650 | 04 |  | Mains transducer-configured, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 1 | 301650 | 04 |  | Mains transducer-configured, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 2 | 301650 | 04 |  | Mains transducer-configured, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 3 | 301650 | 04 |  | Mains transducer-configured, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 4 | 301650 | 04 |  | Mains transducer-configured, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 5 | 301650 | 04 |  | Mains transducer-configured, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 6 | 301650 | 04 |  | Mains transducer-configured, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 7 | 301650 | 04 |  | Mains transducer-configured, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 8 | 301650 | 04 |  | Mains transducer-configured, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 9 | 301650 | 04 |  | Mains transducer-configured, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 10 | 301650 | 04 |  | Mains transducer-configured, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 11 | 301650 | 04 |  | Mains transducer-configured, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 12 | 301650 | 04 |  | Mains transducer-configured, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 13 | 301650 | 04 |  | Mains transducer-configured, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 14 | 301650 | 04 |  | Mains transducer-configured, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1649 | 15 | 301650 | 04 |  | Mains transducer-configured, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 0 | 301651 | 04 |  | TB transducer-configured, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 1 | 301651 | 04 |  | TB transducer-configured, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 2 | 301651 | 04 |  | TB transducer-configured, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 3 | 301651 | 04 |  | TB transducer-configured, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 4 | 301651 | 04 |  | TB transducer-configured, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 5 | 301651 | 04 |  | TB transducer-configured, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 6 | 301651 | 04 |  | TB transducer-configured, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 7 | 301651 | 04 |  | TB transducer-configured, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 8 | 301651 | 04 |  | TB transducer-configured, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 9 | 301651 | 04 |  | TB transducer-configured, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 10 | 301651 | 04 |  | TB transducer-configured, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 11 | 301651 | 04 |  | TB transducer-configured, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 12 | 301651 | 04 |  | TB transducer-configured, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 13 | 301651 | 04 |  | TB transducer-configured, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 14 | 301651 | 04 |  | TB transducer-configured, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1650 | 15 | 301651 | 04 |  | TB transducer-configured, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 0 | 301652 | 04 |  | BTB transducer-configured, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 1 | 301652 | 04 |  | BTB transducer-configured, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 2 | 301652 | 04 |  | BTB transducer-configured, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 3 | 301652 | 04 |  | BTB transducer-configured, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 4 | 301652 | 04 |  | BTB transducer-configured, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 5 | 301652 | 04 |  | BTB transducer-configured, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 6 | 301652 | 04 |  | BTB transducer-configured, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1651 | 7 | 301652 | 04 |  | BTB transducer-configured, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 0 | 301653 | 04 |  | ID 33 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 1 | 301653 | 04 |  | ID 34 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 2 | 301653 | 04 |  | ID 35 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 3 | 301653 | 04 |  | ID 36 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 4 | 301653 | 04 |  | ID 37 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 5 | 301653 | 04 |  | ID 38 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 6 | 301653 | 04 |  | ID 39 BTB controlled | BOOL |  |  |  | X | X
PM Plant logic state | 1652 | 7 | 301653 | 04 |  | ID 40 BTB controlled | BOOL |  |  |  | X | X
PM AC measurement | 1653 |  | 301654 | 04 |  | Nominal power ID 17 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1654 |  | 301655 | 04 |  | Nominal power ID 18 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1655 |  | 301656 | 04 |  | Nominal power ID 19 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1656 |  | 301657 | 04 |  | Nominal power ID 20 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1657 |  | 301658 | 04 |  | Nominal power ID 21 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1658 |  | 301659 | 04 |  | Nominal power ID 22 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1659 |  | 301660 | 04 |  | Nominal power ID 23 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1660 |  | 301661 | 04 |  | Nominal power ID 24 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1661 |  | 301662 | 04 |  | Nominal power ID 25 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1662 |  | 301663 | 04 |  | Nominal power ID 26 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1663 |  | 301664 | 04 |  | Nominal power ID 27 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1664 |  | 301665 | 04 |  | Nominal power ID 28 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1665 |  | 301666 | 04 |  | Nominal power ID 29 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1666 |  | 301667 | 04 |  | Nominal power ID 30 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1667 |  | 301668 | 04 |  | Nominal power ID 31 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1668 |  | 301669 | 04 |  | Nominal power ID 32 | INT16s | AB | 0 |  | X | X
PM AC measurement | 1696 |  | 301697 | 04 |  | PV active power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1697 |  | 301698 | 04 |  | PV reactive power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1698 |  | 301699 | 04 |  | Battery active power | INT16s | AB | 0 |  | X | X
PM AC measurement | 1699 |  | 301700 | 04 |  | Battery reactive power | INT16s | AB | 0 |  | X | X
PM Plant logic state | 1700 | 0 | 301701 | 04 |  | TB available | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 1 | 301701 | 04 |  | Mains unit available | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 2 | 301701 | 04 |  | Any MB pos. ON | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 3 | 301701 | 04 |  | All MB pos. OFF | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 4 | 301701 | 04 |  | TB pos. ON (Mains Command Unit) | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 5 | 301701 | 04 |  | TB pos. OFF (Mains Command Unit) | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 6 | 301701 | 04 |  | Any GB pos. ON | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 7 | 301701 | 04 |  | All GB pos. OFF | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 8 | 301701 | 04 |  | Any TB pos. ON | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 9 | 301701 | 04 |  | All TB pos. OFF | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 10 | 301701 | 04 |  | Any BTB pos. ON | BOOL |  |  |  | X | X
PM Plant logic state | 1700 | 11 | 301701 | 04 |  | Any BTB pos. OFF | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 0 | 301702 | 04 |  | GB pos. ON ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 1 | 301702 | 04 |  | GB pos. ON ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 2 | 301702 | 04 |  | GB pos. ON ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 3 | 301702 | 04 |  | GB pos. ON ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 4 | 301702 | 04 |  | GB pos. ON ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 5 | 301702 | 04 |  | GB pos. ON ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 6 | 301702 | 04 |  | GB pos. ON ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 7 | 301702 | 04 |  | GB pos. ON ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 8 | 301702 | 04 |  | GB pos. ON ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 9 | 301702 | 04 |  | GB pos. ON ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 10 | 301702 | 04 |  | GB pos. ON ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 11 | 301702 | 04 |  | GB pos. ON ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 12 | 301702 | 04 |  | GB pos. ON ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 13 | 301702 | 04 |  | GB pos. ON ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 14 | 301702 | 04 |  | GB pos. ON ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1701 | 15 | 301702 | 04 |  | GB pos. ON ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 0 | 301703 | 04 |  | GB pos. OFF ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 1 | 301703 | 04 |  | GB pos. OFF ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 2 | 301703 | 04 |  | GB pos. OFF ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 3 | 301703 | 04 |  | GB pos. OFF ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 4 | 301703 | 04 |  | GB pos. OFF ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 5 | 301703 | 04 |  | GB pos. OFF ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 6 | 301703 | 04 |  | GB pos. OFF ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 7 | 301703 | 04 |  | GB pos. OFF ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 8 | 301703 | 04 |  | GB pos. OFF ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 9 | 301703 | 04 |  | GB pos. OFF ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 10 | 301703 | 04 |  | GB pos. OFF ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 11 | 301703 | 04 |  | GB pos. OFF ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 12 | 301703 | 04 |  | GB pos. OFF ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 13 | 301703 | 04 |  | GB pos. OFF ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 14 | 301703 | 04 |  | GB pos. OFF ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1702 | 15 | 301703 | 04 |  | GB pos. OFF ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 0 | 301704 | 04 |  | DG Hz/V OK, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 1 | 301704 | 04 |  | DG Hz/V OK, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 2 | 301704 | 04 |  | DG Hz/V OK, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 3 | 301704 | 04 |  | DG Hz/V OK, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 4 | 301704 | 04 |  | DG Hz/V OK, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 5 | 301704 | 04 |  | DG Hz/V OK, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 6 | 301704 | 04 |  | DG Hz/V OK, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 7 | 301704 | 04 |  | DG Hz/V OK, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 8 | 301704 | 04 |  | DG Hz/V OK, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 9 | 301704 | 04 |  | DG Hz/V OK, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 10 | 301704 | 04 |  | DG Hz/V OK, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 11 | 301704 | 04 |  | DG Hz/V OK, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 12 | 301704 | 04 |  | DG Hz/V OK, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 13 | 301704 | 04 |  | DG Hz/V OK, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 14 | 301704 | 04 |  | DG Hz/V OK, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1703 | 15 | 301704 | 04 |  | DG Hz/V OK, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 0 | 301705 | 04 |  | Mains OK, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 1 | 301705 | 04 |  | Mains OK, mains 1A | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 2 | 301705 | 04 |  | Mains OK, mains 1B | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 3 | 301705 | 04 |  | Mains OK, mains 2A | BOOL |  |  |  | X | X
PM Plant logic state | 1704 | 4 | 301705 | 04 |  | Mains OK, mains 2B | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 0 | 301706 | 04 |  | Ready for auto start, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 1 | 301706 | 04 |  | Ready for auto start, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 2 | 301706 | 04 |  | Ready for auto start, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 3 | 301706 | 04 |  | Ready for auto start, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 4 | 301706 | 04 |  | Ready for auto start, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 5 | 301706 | 04 |  | Ready for auto start, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 6 | 301706 | 04 |  | Ready for auto start, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 7 | 301706 | 04 |  | Ready for auto start, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 8 | 301706 | 04 |  | Ready for auto start, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 9 | 301706 | 04 |  | Ready for auto start, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 10 | 301706 | 04 |  | Ready for auto start, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 11 | 301706 | 04 |  | Ready for auto start, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 12 | 301706 | 04 |  | Ready for auto start, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 13 | 301706 | 04 |  | Ready for auto start, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 14 | 301706 | 04 |  | Ready for auto start, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1705 | 15 | 301706 | 04 |  | Ready for auto start, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 0 | 301707 | 04 |  | Mains not in semi, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 1 | 301707 | 04 |  | Mains not in semi, mains 1A | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 2 | 301707 | 04 |  | Mains not in semi, mains 1B | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 3 | 301707 | 04 |  | Mains not in semi, mains 2A | BOOL |  |  |  | X | X
PM Plant logic state | 1706 | 4 | 301707 | 04 |  | Mains not in semi, mains 2B | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 0 | 301708 | 04 |  | Any alarms, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 1 | 301708 | 04 |  | Any alarms, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 2 | 301708 | 04 |  | Any alarms, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 3 | 301708 | 04 |  | Any alarms, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 4 | 301708 | 04 |  | Any alarms, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 5 | 301708 | 04 |  | Any alarms, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 6 | 301708 | 04 |  | Any alarms, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 7 | 301708 | 04 |  | Any alarms, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 8 | 301708 | 04 |  | Any alarms, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 9 | 301708 | 04 |  | Any alarms, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 10 | 301708 | 04 |  | Any alarms, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 11 | 301708 | 04 |  | Any alarms, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 12 | 301708 | 04 |  | Any alarms, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 13 | 301708 | 04 |  | Any alarms, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 14 | 301708 | 04 |  | Any alarms, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1707 | 15 | 301708 | 04 |  | Any alarms, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 0 | 301709 | 04 |  | Any alarms, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 1 | 301709 | 04 |  | Any alarms, mains 1A | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 2 | 301709 | 04 |  | Any alarms, mains 1B | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 3 | 301709 | 04 |  | Any alarms, mains 2A | BOOL |  |  |  | X | X
PM Plant logic state | 1708 | 4 | 301709 | 04 |  | Any alarms, mains 2B | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 0 | 301710 | 04 |  | Engine running, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 1 | 301710 | 04 |  | Engine running, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 2 | 301710 | 04 |  | Engine running, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 3 | 301710 | 04 |  | Engine running, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 4 | 301710 | 04 |  | Engine running, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 5 | 301710 | 04 |  | Engine running, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 6 | 301710 | 04 |  | Engine running, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 7 | 301710 | 04 |  | Engine running, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 8 | 301710 | 04 |  | Engine running, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 9 | 301710 | 04 |  | Engine running, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 10 | 301710 | 04 |  | Engine running, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 11 | 301710 | 04 |  | Engine running, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 12 | 301710 | 04 |  | Engine running, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 13 | 301710 | 04 |  | Engine running, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 14 | 301710 | 04 |  | Engine running, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1709 | 15 | 301710 | 04 |  | Engine running, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 0 | 301711 | 04 |  | MB pos. ON, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 1 | 301711 | 04 |  | MB pos. ON, mains 1A | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 2 | 301711 | 04 |  | MB pos. ON, mains 1B | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 3 | 301711 | 04 |  | MB pos. ON, mains 2A | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 4 | 301711 | 04 |  | MB pos. ON, mains 2B | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 5 | 301711 | 04 |  | MB pos. OFF, single mains | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 6 | 301711 | 04 |  | MB pos. OFF, mains 1A | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 7 | 301711 | 04 |  | MB pos. OFF, mains 1B | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 8 | 301711 | 04 |  | MB pos. OFF, mains 2A | BOOL |  |  |  | X | X
PM Plant logic state | 1710 | 9 | 301711 | 04 |  | MB pos. OFF, mains 2B | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 0 | 301712 | 04 |  | GB synchronising, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 1 | 301712 | 04 |  | GB synchronising, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 2 | 301712 | 04 |  | GB synchronising, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 3 | 301712 | 04 |  | GB synchronising, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 4 | 301712 | 04 |  | GB synchronising, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 5 | 301712 | 04 |  | GB synchronising, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 6 | 301712 | 04 |  | GB synchronising, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 7 | 301712 | 04 |  | GB synchronising, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 8 | 301712 | 04 |  | GB synchronising, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 9 | 301712 | 04 |  | GB synchronising, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 10 | 301712 | 04 |  | GB synchronising, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 11 | 301712 | 04 |  | GB synchronising, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 12 | 301712 | 04 |  | GB synchronising, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 13 | 301712 | 04 |  | GB synchronising, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 14 | 301712 | 04 |  | GB synchronising, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1711 | 15 | 301712 | 04 |  | GB synchronising, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 0 | 301713 | 04 |  | Mains OK, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 1 | 301713 | 04 |  | Mains OK, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 2 | 301713 | 04 |  | Mains OK, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 3 | 301713 | 04 |  | Mains OK, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 4 | 301713 | 04 |  | Mains OK, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 5 | 301713 | 04 |  | Mains OK, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 6 | 301713 | 04 |  | Mains OK, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 7 | 301713 | 04 |  | Mains OK, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 8 | 301713 | 04 |  | Mains OK, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 9 | 301713 | 04 |  | Mains OK, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 10 | 301713 | 04 |  | Mains OK, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 11 | 301713 | 04 |  | Mains OK, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 12 | 301713 | 04 |  | Mains OK, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 13 | 301713 | 04 |  | Mains OK, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 14 | 301713 | 04 |  | Mains OK, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1712 | 15 | 301713 | 04 |  | Mains OK, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 0 | 301714 | 04 |  | Mains not in semi 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 1 | 301714 | 04 |  | Mains not in semi 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 2 | 301714 | 04 |  | Mains not in semi 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 3 | 301714 | 04 |  | Mains not in semi 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 4 | 301714 | 04 |  | Mains not in semi 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 5 | 301714 | 04 |  | Mains not in semi 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 6 | 301714 | 04 |  | Mains not in semi 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 7 | 301714 | 04 |  | Mains not in semi 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 8 | 301714 | 04 |  | Mains not in semi 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 9 | 301714 | 04 |  | Mains not in semi 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 10 | 301714 | 04 |  | Mains not in semi 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 11 | 301714 | 04 |  | Mains not in semi 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 12 | 301714 | 04 |  | Mains not in semi 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 13 | 301714 | 04 |  | Mains not in semi 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 14 | 301714 | 04 |  | Mains not in semi 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1713 | 15 | 301714 | 04 |  | Mains not in semi 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 0 | 301715 | 04 |  | Any alarms, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 1 | 301715 | 04 |  | Any alarms, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 2 | 301715 | 04 |  | Any alarms, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 3 | 301715 | 04 |  | Any alarms, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 4 | 301715 | 04 |  | Any alarms, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 5 | 301715 | 04 |  | Any alarms, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 6 | 301715 | 04 |  | Any alarms, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 7 | 301715 | 04 |  | Any alarms, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 8 | 301715 | 04 |  | Any alarms, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 9 | 301715 | 04 |  | Any alarms, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 10 | 301715 | 04 |  | Any alarms, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 11 | 301715 | 04 |  | Any alarms, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 12 | 301715 | 04 |  | Any alarms, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 13 | 301715 | 04 |  | Any alarms, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 14 | 301715 | 04 |  | Any alarms, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1714 | 15 | 301715 | 04 |  | Any alarms, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 0 | 301716 | 04 |  | MB pos. ON, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 1 | 301716 | 04 |  | MB pos. ON, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 2 | 301716 | 04 |  | MB pos. ON, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 3 | 301716 | 04 |  | MB pos. ON, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 4 | 301716 | 04 |  | MB pos. ON, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 5 | 301716 | 04 |  | MB pos. ON, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 6 | 301716 | 04 |  | MB pos. ON, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 7 | 301716 | 04 |  | MB pos. ON, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 8 | 301716 | 04 |  | MB pos. ON, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 9 | 301716 | 04 |  | MB pos. ON, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 10 | 301716 | 04 |  | MB pos. ON, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 11 | 301716 | 04 |  | MB pos. ON, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 12 | 301716 | 04 |  | MB pos. ON, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 13 | 301716 | 04 |  | MB pos. ON, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 14 | 301716 | 04 |  | MB pos. ON, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1715 | 15 | 301716 | 04 |  | MB pos. ON, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 0 | 301717 | 04 |  | MB pos. OFF, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 1 | 301717 | 04 |  | MB pos. OFF, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 2 | 301717 | 04 |  | MB pos. OFF, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 3 | 301717 | 04 |  | MB pos. OFF, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 4 | 301717 | 04 |  | MB pos. OFF, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 5 | 301717 | 04 |  | MB pos. OFF, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 6 | 301717 | 04 |  | MB pos. OFF, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 7 | 301717 | 04 |  | MB pos. OFF, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 8 | 301717 | 04 |  | MB pos. OFF, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 9 | 301717 | 04 |  | MB pos. OFF, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 10 | 301717 | 04 |  | MB pos. OFF, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 11 | 301717 | 04 |  | MB pos. OFF, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 12 | 301717 | 04 |  | MB pos. OFF, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 13 | 301717 | 04 |  | MB pos. OFF, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 14 | 301717 | 04 |  | MB pos. OFF, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1716 | 15 | 301717 | 04 |  | MB pos. OFF, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 0 | 301718 | 04 |  | Mains failure, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 1 | 301718 | 04 |  | Mains failure, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 2 | 301718 | 04 |  | Mains failure, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 3 | 301718 | 04 |  | Mains failure, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 4 | 301718 | 04 |  | Mains failure, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 5 | 301718 | 04 |  | Mains failure, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 6 | 301718 | 04 |  | Mains failure, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 7 | 301718 | 04 |  | Mains failure, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 8 | 301718 | 04 |  | Mains failure, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 9 | 301718 | 04 |  | Mains failure, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 10 | 301718 | 04 |  | Mains failure, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 11 | 301718 | 04 |  | Mains failure, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 12 | 301718 | 04 |  | Mains failure, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 13 | 301718 | 04 |  | Mains failure, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 14 | 301718 | 04 |  | Mains failure, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1717 | 15 | 301718 | 04 |  | Mains failure, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 0 | 301719 | 04 |  | MB synchronising, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 1 | 301719 | 04 |  | MB synchronising, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 2 | 301719 | 04 |  | MB synchronising, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 3 | 301719 | 04 |  | MB synchronising, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 4 | 301719 | 04 |  | MB synchronising, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 5 | 301719 | 04 |  | MB synchronising, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 6 | 301719 | 04 |  | MB synchronising, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 7 | 301719 | 04 |  | MB synchronising, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 8 | 301719 | 04 |  | MB synchronising, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 9 | 301719 | 04 |  | MB synchronising, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 10 | 301719 | 04 |  | MB synchronising, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 11 | 301719 | 04 |  | MB synchronising, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 12 | 301719 | 04 |  | MB synchronising, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 13 | 301719 | 04 |  | MB synchronising, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 14 | 301719 | 04 |  | MB synchronising, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1718 | 15 | 301719 | 04 |  | MB synchronising, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 0 | 301720 | 04 |  | TB pos. ON, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 1 | 301720 | 04 |  | TB pos. ON, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 2 | 301720 | 04 |  | TB pos. ON, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 3 | 301720 | 04 |  | TB pos. ON, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 4 | 301720 | 04 |  | TB pos. ON, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 5 | 301720 | 04 |  | TB pos. ON, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 6 | 301720 | 04 |  | TB pos. ON, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 7 | 301720 | 04 |  | TB pos. ON, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 8 | 301720 | 04 |  | TB pos. ON, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 9 | 301720 | 04 |  | TB pos. ON, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 10 | 301720 | 04 |  | TB pos. ON, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 11 | 301720 | 04 |  | TB pos. ON, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 12 | 301720 | 04 |  | TB pos. ON, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 13 | 301720 | 04 |  | TB pos. ON, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 14 | 301720 | 04 |  | TB pos. ON, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1719 | 15 | 301720 | 04 |  | TB pos. ON, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 0 | 301721 | 04 |  | TB pos. OFF, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 1 | 301721 | 04 |  | TB pos. OFF, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 2 | 301721 | 04 |  | TB pos. OFF, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 3 | 301721 | 04 |  | TB pos. OFF, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 4 | 301721 | 04 |  | TB pos. OFF, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 5 | 301721 | 04 |  | TB pos. OFF, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 6 | 301721 | 04 |  | TB pos. OFF, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 7 | 301721 | 04 |  | TB pos. OFF, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 8 | 301721 | 04 |  | TB pos. OFF, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 9 | 301721 | 04 |  | TB pos. OFF, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 10 | 301721 | 04 |  | TB pos. OFF, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 11 | 301721 | 04 |  | TB pos. OFF, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 12 | 301721 | 04 |  | TB pos. OFF, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 13 | 301721 | 04 |  | TB pos. OFF, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 14 | 301721 | 04 |  | TB pos. OFF, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1720 | 15 | 301721 | 04 |  | TB pos. OFF, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 0 | 301722 | 04 |  | TB synchronising, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 1 | 301722 | 04 |  | TB synchronising, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 2 | 301722 | 04 |  | TB synchronising, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 3 | 301722 | 04 |  | TB synchronising, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 4 | 301722 | 04 |  | TB synchronising, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 5 | 301722 | 04 |  | TB synchronising, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 6 | 301722 | 04 |  | TB synchronising, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 7 | 301722 | 04 |  | TB synchronising, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 8 | 301722 | 04 |  | TB synchronising, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 9 | 301722 | 04 |  | TB synchronising, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 10 | 301722 | 04 |  | TB synchronising, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 11 | 301722 | 04 |  | TB synchronising, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 12 | 301722 | 04 |  | TB synchronising, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 13 | 301722 | 04 |  | TB synchronising, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 14 | 301722 | 04 |  | TB synchronising, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1721 | 15 | 301722 | 04 |  | TB synchronising, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 0 | 301723 | 04 |  | Any alarms, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 1 | 301723 | 04 |  | Any alarms, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 2 | 301723 | 04 |  | Any alarms, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 3 | 301723 | 04 |  | Any alarms, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 4 | 301723 | 04 |  | Any alarms, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 5 | 301723 | 04 |  | Any alarms, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 6 | 301723 | 04 |  | Any alarms, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1722 | 7 | 301723 | 04 |  | Any alarms, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 0 | 301726 | 04 |  | BTB synchronising, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 1 | 301726 | 04 |  | BTB synchronising, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 2 | 301726 | 04 |  | BTB synchronising, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 3 | 301726 | 04 |  | BTB synchronising, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 4 | 301726 | 04 |  | BTB synchronising, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 5 | 301726 | 04 |  | BTB synchronising, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 6 | 301726 | 04 |  | BTB synchronising, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1725 | 7 | 301726 | 04 |  | BTB synchronising, ID 40 | BOOL |  |  |  | X | X
PM alarm | 1727 | 0 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 17 | BOOL |  |  |  | X | X
PM alarm | 1727 | 1 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 18 | BOOL |  |  |  | X | X
PM alarm | 1727 | 2 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 19 | BOOL |  |  |  | X | X
PM alarm | 1727 | 3 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 20 | BOOL |  |  |  | X | X
PM alarm | 1727 | 4 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 21 | BOOL |  |  |  | X | X
PM alarm | 1727 | 5 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 22 | BOOL |  |  |  | X | X
PM alarm | 1727 | 6 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 23 | BOOL |  |  |  | X | X
PM alarm | 1727 | 7 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 24 | BOOL |  |  |  | X | X
PM alarm | 1727 | 8 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 25 | BOOL |  |  |  | X | X
PM alarm | 1727 | 9 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 26 | BOOL |  |  |  | X | X
PM alarm | 1727 | 10 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 27 | BOOL |  |  |  | X | X
PM alarm | 1727 | 11 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 28 | BOOL |  |  |  | X | X
PM alarm | 1727 | 12 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 29 | BOOL |  |  |  | X | X
PM alarm | 1727 | 13 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 30 | BOOL |  |  |  | X | X
PM alarm | 1727 | 14 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 31 | BOOL |  |  |  | X | X
PM alarm | 1727 | 15 | 301728 | 04 |  | Ext. Modbus comm. error, CAN ID 32 | BOOL |  |  |  | X | X
PM alarm | 1728 | 0 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 33 | BOOL |  |  |  | X | X
PM alarm | 1728 | 1 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 34 | BOOL |  |  |  | X | X
PM alarm | 1728 | 2 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 35 | BOOL |  |  |  | X | X
PM alarm | 1728 | 3 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 36 | BOOL |  |  |  | X | X
PM alarm | 1728 | 4 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 37 | BOOL |  |  |  | X | X
PM alarm | 1728 | 5 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 38 | BOOL |  |  |  | X | X
PM alarm | 1728 | 6 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 39 | BOOL |  |  |  | X | X
PM alarm | 1728 | 7 | 301729 | 04 |  | Ext. Modbus comm. error, CAN ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 0 | 301733 | 04 |  | BB Hz/V OK, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 1 | 301733 | 04 |  | BB Hz/V OK, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 2 | 301733 | 04 |  | BB Hz/V OK, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 3 | 301733 | 04 |  | BB Hz/V OK, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 4 | 301733 | 04 |  | BB Hz/V OK, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 5 | 301733 | 04 |  | BB Hz/V OK, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 6 | 301733 | 04 |  | BB Hz/V OK, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 7 | 301733 | 04 |  | BB Hz/V OK, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 8 | 301733 | 04 |  | BB Hz/V OK, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 9 | 301733 | 04 |  | BB Hz/V OK, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 10 | 301733 | 04 |  | BB Hz/V OK, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 11 | 301733 | 04 |  | BB Hz/V OK, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 12 | 301733 | 04 |  | BB Hz/V OK, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 13 | 301733 | 04 |  | BB Hz/V OK, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 14 | 301733 | 04 |  | BB Hz/V OK, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1732 | 15 | 301733 | 04 |  | BB Hz/V OK, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 0 | 301734 | 04 |  | BB Hz/V OK, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 1 | 301734 | 04 |  | BB Hz/V OK, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 2 | 301734 | 04 |  | BB Hz/V OK, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 3 | 301734 | 04 |  | BB Hz/V OK, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 4 | 301734 | 04 |  | BB Hz/V OK, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 5 | 301734 | 04 |  | BB Hz/V OK, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 6 | 301734 | 04 |  | BB Hz/V OK, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 7 | 301734 | 04 |  | BB Hz/V OK, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 8 | 301734 | 04 |  | BB Hz/V OK, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 9 | 301734 | 04 |  | BB Hz/V OK, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 10 | 301734 | 04 |  | BB Hz/V OK, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 11 | 301734 | 04 |  | BB Hz/V OK, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 12 | 301734 | 04 |  | BB Hz/V OK, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 13 | 301734 | 04 |  | BB Hz/V OK, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 14 | 301734 | 04 |  | BB Hz/V OK, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1733 | 15 | 301734 | 04 |  | BB Hz/V OK, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 0 | 301735 | 04 |  | BB Hz/V OK, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 1 | 301735 | 04 |  | BB Hz/V OK, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 2 | 301735 | 04 |  | BB Hz/V OK, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 3 | 301735 | 04 |  | BB Hz/V OK, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 4 | 301735 | 04 |  | BB Hz/V OK, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 5 | 301735 | 04 |  | BB Hz/V OK, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 6 | 301735 | 04 |  | BB Hz/V OK, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1734 | 7 | 301735 | 04 |  | BB Hz/V OK, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 0 | 301736 | 04 |  | BB Hz/V present, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 1 | 301736 | 04 |  | BB Hz/V present, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 2 | 301736 | 04 |  | BB Hz/V present, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 3 | 301736 | 04 |  | BB Hz/V present, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 4 | 301736 | 04 |  | BB Hz/V present, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 5 | 301736 | 04 |  | BB Hz/V present, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 6 | 301736 | 04 |  | BB Hz/V present, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 7 | 301736 | 04 |  | BB Hz/V present, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 8 | 301736 | 04 |  | BB Hz/V present, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 9 | 301736 | 04 |  | BB Hz/V present, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 10 | 301736 | 04 |  | BB Hz/V present, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 11 | 301736 | 04 |  | BB Hz/V present, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 12 | 301736 | 04 |  | BB Hz/V present, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 13 | 301736 | 04 |  | BB Hz/V present, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 14 | 301736 | 04 |  | BB Hz/V present, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1735 | 15 | 301736 | 04 |  | BB Hz/V present, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 0 | 301737 | 04 |  | BB Hz/V present, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 1 | 301737 | 04 |  | BB Hz/V present, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 2 | 301737 | 04 |  | BB Hz/V present, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 3 | 301737 | 04 |  | BB Hz/V present, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 4 | 301737 | 04 |  | BB Hz/V present, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 5 | 301737 | 04 |  | BB Hz/V present, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 6 | 301737 | 04 |  | BB Hz/V present, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 7 | 301737 | 04 |  | BB Hz/V present, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 8 | 301737 | 04 |  | BB Hz/V present, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 9 | 301737 | 04 |  | BB Hz/V present, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 10 | 301737 | 04 |  | BB Hz/V present, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 11 | 301737 | 04 |  | BB Hz/V present, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 12 | 301737 | 04 |  | BB Hz/V present, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 13 | 301737 | 04 |  | BB Hz/V present, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 14 | 301737 | 04 |  | BB Hz/V present, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1736 | 15 | 301737 | 04 |  | BB Hz/V present, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 0 | 301738 | 04 |  | BB Hz/V present, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 1 | 301738 | 04 |  | BB Hz/V present, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 2 | 301738 | 04 |  | BB Hz/V present, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 3 | 301738 | 04 |  | BB Hz/V present, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 4 | 301738 | 04 |  | BB Hz/V present, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 5 | 301738 | 04 |  | BB Hz/V present, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 6 | 301738 | 04 |  | BB Hz/V present, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1737 | 7 | 301738 | 04 |  | BB Hz/V present, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 0 | 301739 | 04 |  | BA Hz/V OK, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 1 | 301739 | 04 |  | BA Hz/V OK, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 2 | 301739 | 04 |  | BA Hz/V OK, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 3 | 301739 | 04 |  | BA Hz/V OK, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 4 | 301739 | 04 |  | BA Hz/V OK, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 5 | 301739 | 04 |  | BA Hz/V OK, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 6 | 301739 | 04 |  | BA Hz/V OK, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1738 | 7 | 301739 | 04 |  | BA Hz/V OK, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 0 | 301740 | 04 |  | DG Hz/V present, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 1 | 301740 | 04 |  | DG Hz/V present, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 2 | 301740 | 04 |  | DG Hz/V present, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 3 | 301740 | 04 |  | DG Hz/V present, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 4 | 301740 | 04 |  | DG Hz/V present, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 5 | 301740 | 04 |  | DG Hz/V present, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 6 | 301740 | 04 |  | DG Hz/V present, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 7 | 301740 | 04 |  | DG Hz/V present, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 8 | 301740 | 04 |  | DG Hz/V present, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 9 | 301740 | 04 |  | DG Hz/V present, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 10 | 301740 | 04 |  | DG Hz/V present, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 11 | 301740 | 04 |  | DG Hz/V present, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 12 | 301740 | 04 |  | DG Hz/V present, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 13 | 301740 | 04 |  | DG Hz/V present, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 14 | 301740 | 04 |  | DG Hz/V present, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1739 | 15 | 301740 | 04 |  | DG Hz/V present, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 0 | 301741 | 04 |  | Hz/V present, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 1 | 301741 | 04 |  | Hz/V present, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 2 | 301741 | 04 |  | Hz/V present, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 3 | 301741 | 04 |  | Hz/V present, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 4 | 301741 | 04 |  | Hz/V present, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 5 | 301741 | 04 |  | Hz/V present, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 6 | 301741 | 04 |  | Hz/V present, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 7 | 301741 | 04 |  | Hz/V present, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 8 | 301741 | 04 |  | Hz/V present, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 9 | 301741 | 04 |  | Hz/V present, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 10 | 301741 | 04 |  | Hz/V present, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 11 | 301741 | 04 |  | Hz/V present, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 12 | 301741 | 04 |  | Hz/V present, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 13 | 301741 | 04 |  | Hz/V present, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 14 | 301741 | 04 |  | Hz/V present, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1740 | 15 | 301741 | 04 |  | Hz/V present, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 0 | 301742 | 04 |  | BA Hz/V present, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 1 | 301742 | 04 |  | BA Hz/V present, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 2 | 301742 | 04 |  | BA Hz/V present, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 3 | 301742 | 04 |  | BA Hz/V present, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 4 | 301742 | 04 |  | BA Hz/V present, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 5 | 301742 | 04 |  | BA Hz/V present, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 6 | 301742 | 04 |  | BA Hz/V present, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1741 | 7 | 301742 | 04 |  | BA Hz/V present, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 0 | 301744 | 04 |  | Redundant backup present ID1 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 1 | 301744 | 04 |  | Redundant backup present ID2 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 2 | 301744 | 04 |  | Redundant backup present ID3 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 3 | 301744 | 04 |  | Redundant backup present ID4 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 4 | 301744 | 04 |  | Redundant backup present ID5 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 5 | 301744 | 04 |  | Redundant backup present ID6 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 6 | 301744 | 04 |  | Redundant backup present ID7 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 7 | 301744 | 04 |  | Redundant backup present ID8 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 8 | 301744 | 04 |  | Redundant backup present ID9 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 9 | 301744 | 04 |  | Redundant backup present ID10 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 10 | 301744 | 04 |  | Redundant backup present ID11 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 11 | 301744 | 04 |  | Redundant backup present ID12 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 12 | 301744 | 04 |  | Redundant backup present ID13 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 13 | 301744 | 04 |  | Redundant backup present ID14 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 14 | 301744 | 04 |  | Redundant backup present ID15 | BOOL |  |  |  | X | X
PM Plant logic state | 1743 | 15 | 301744 | 04 |  | Redundant backup present ID16 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 0 | 301747 | 04 |  | Controller B active on ID1 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 1 | 301747 | 04 |  | Controller B active on ID2 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 2 | 301747 | 04 |  | Controller B active on ID3 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 3 | 301747 | 04 |  | Controller B active on ID4 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 4 | 301747 | 04 |  | Controller B active on ID5 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 5 | 301747 | 04 |  | Controller B active on ID6 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 6 | 301747 | 04 |  | Controller B active on ID7 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 7 | 301747 | 04 |  | Controller B active on ID8 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 8 | 301747 | 04 |  | Controller B active on ID9 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 9 | 301747 | 04 |  | Controller B active on ID10 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 10 | 301747 | 04 |  | Controller B active on ID11 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 11 | 301747 | 04 |  | Controller B active on ID12 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 12 | 301747 | 04 |  | Controller B active on ID13 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 13 | 301747 | 04 |  | Controller B active on ID14 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 14 | 301747 | 04 |  | Controller B active on ID15 | BOOL |  |  |  | X | X
PM Plant logic state | 1746 | 15 | 301747 | 04 |  | Controller B active on ID16 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 0 | 301748 | 04 |  | Controller B active on ID17 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 1 | 301748 | 04 |  | Controller B active on ID18 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 2 | 301748 | 04 |  | Controller B active on ID19 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 3 | 301748 | 04 |  | Controller B active on ID20 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 4 | 301748 | 04 |  | Controller B active on ID21 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 5 | 301748 | 04 |  | Controller B active on ID22 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 6 | 301748 | 04 |  | Controller B active on ID23 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 7 | 301748 | 04 |  | Controller B active on ID24 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 8 | 301748 | 04 |  | Controller B active on ID25 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 9 | 301748 | 04 |  | Controller B active on ID26 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 10 | 301748 | 04 |  | Controller B active on ID27 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 11 | 301748 | 04 |  | Controller B active on ID28 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 12 | 301748 | 04 |  | Controller B active on ID29 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 13 | 301748 | 04 |  | Controller B active on ID30 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 14 | 301748 | 04 |  | Controller B active on ID31 | BOOL |  |  |  | X | X
PM Plant logic state | 1747 | 15 | 301748 | 04 |  | Controller B active on ID32 | BOOL |  |  |  | X | X
PM Plant logic state | 1748 | 0 | 301749 | 04 |  | Controller B active on ID33 | BOOL |  |  |  | X | X
PM Plant logic state | 1748 | 1 | 301749 | 04 |  | Controller B active on ID34 | BOOL |  |  |  | X | X
PM Plant logic state | 1748 | 2 | 301749 | 04 |  | Controller B active on ID35 | BOOL |  |  |  | X | X
PM Plant logic state | 1748 | 3 | 301749 | 04 |  | Controller B active on ID36 | BOOL |  |  |  | X | X
PM Plant logic state | 1748 | 4 | 301749 | 04 |  | Controller B active on ID37 | BOOL |  |  |  | X | X
PM Plant logic state | 1748 | 5 | 301749 | 04 |  | Controller B active on ID38 | BOOL |  |  |  | X | X
PM Plant logic state | 1748 | 6 | 301749 | 04 |  | Controller B active on ID39 | BOOL |  |  |  | X | X
PM Plant logic state | 1748 | 7 | 301749 | 04 |  | Controller B active on ID40 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 0 | 301750 | 04 |  | Dry Mode active on ID1 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 1 | 301750 | 04 |  | Dry Mode active on ID2 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 2 | 301750 | 04 |  | Dry Mode active on ID3 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 3 | 301750 | 04 |  | Dry Mode active on ID4 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 4 | 301750 | 04 |  | Dry Mode active on ID5 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 5 | 301750 | 04 |  | Dry Mode active on ID6 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 6 | 301750 | 04 |  | Dry Mode active on ID7 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 7 | 301750 | 04 |  | Dry Mode active on ID8 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 8 | 301750 | 04 |  | Dry Mode active on ID9 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 9 | 301750 | 04 |  | Dry Mode active on ID10 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 10 | 301750 | 04 |  | Dry Mode active on ID11 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 11 | 301750 | 04 |  | Dry Mode active on ID12 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 12 | 301750 | 04 |  | Dry Mode active on ID13 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 13 | 301750 | 04 |  | Dry Mode active on ID14 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 14 | 301750 | 04 |  | Dry Mode active on ID15 | BOOL |  |  |  | X | X
PM Plant logic state | 1749 | 15 | 301750 | 04 |  | Dry Mode active on ID16 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 0 | 301751 | 04 |  | GB Pos ON, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 1 | 301751 | 04 |  | GB Pos ON, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 2 | 301751 | 04 |  | GB Pos ON, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 3 | 301751 | 04 |  | GB Pos ON, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 4 | 301751 | 04 |  | GB Pos ON, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 5 | 301751 | 04 |  | GB Pos ON, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 6 | 301751 | 04 |  | GB Pos ON, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 7 | 301751 | 04 |  | GB Pos ON, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 8 | 301751 | 04 |  | GB Pos ON, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 9 | 301751 | 04 |  | GB Pos ON, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 10 | 301751 | 04 |  | GB Pos ON, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 11 | 301751 | 04 |  | GB Pos ON, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 12 | 301751 | 04 |  | GB Pos ON, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 13 | 301751 | 04 |  | GB Pos ON, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 14 | 301751 | 04 |  | GB Pos ON, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1750 | 15 | 301751 | 04 |  | GB Pos ON, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 0 | 301752 | 04 |  | GB Pos OFF, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 1 | 301752 | 04 |  | GB Pos OFF, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 2 | 301752 | 04 |  | GB Pos OFF, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 3 | 301752 | 04 |  | GB Pos OFF, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 4 | 301752 | 04 |  | GB Pos OFF, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 5 | 301752 | 04 |  | GB Pos OFF, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 6 | 301752 | 04 |  | GB Pos OFF, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 7 | 301752 | 04 |  | GB Pos OFF, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 8 | 301752 | 04 |  | GB Pos OFF, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 9 | 301752 | 04 |  | GB Pos OFF, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 10 | 301752 | 04 |  | GB Pos OFF, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 11 | 301752 | 04 |  | GB Pos OFF, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 12 | 301752 | 04 |  | GB Pos OFF, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 13 | 301752 | 04 |  | GB Pos OFF, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 14 | 301752 | 04 |  | GB Pos OFF, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1751 | 15 | 301752 | 04 |  | GB Pos OFF, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 0 | 301753 | 04 |  | GB synchronising, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 1 | 301753 | 04 |  | GB synchronising, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 2 | 301753 | 04 |  | GB synchronising, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 3 | 301753 | 04 |  | GB synchronising, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 4 | 301753 | 04 |  | GB synchronising, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 5 | 301753 | 04 |  | GB synchronising, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 6 | 301753 | 04 |  | GB synchronising, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 7 | 301753 | 04 |  | GB synchronising, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 8 | 301753 | 04 |  | GB synchronising, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 9 | 301753 | 04 |  | GB synchronising, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 10 | 301753 | 04 |  | GB synchronising, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 11 | 301753 | 04 |  | GB synchronising, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 12 | 301753 | 04 |  | GB synchronising, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 13 | 301753 | 04 |  | GB synchronising, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 14 | 301753 | 04 |  | GB synchronising, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1752 | 15 | 301753 | 04 |  | GB synchronising, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 0 | 301754 | 04 |  | Hz/V OK, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 1 | 301754 | 04 |  | Hz/V OK, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 2 | 301754 | 04 |  | Hz/V OK, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 3 | 301754 | 04 |  | Hz/V OK, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 4 | 301754 | 04 |  | Hz/V OK, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 5 | 301754 | 04 |  | Hz/V OK, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 6 | 301754 | 04 |  | Hz/V OK, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 7 | 301754 | 04 |  | Hz/V OK, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 8 | 301754 | 04 |  | Hz/V OK, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 9 | 301754 | 04 |  | Hz/V OK, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 10 | 301754 | 04 |  | Hz/V OK, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 11 | 301754 | 04 |  | Hz/V OK, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 12 | 301754 | 04 |  | Hz/V OK, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 13 | 301754 | 04 |  | Hz/V OK, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 14 | 301754 | 04 |  | Hz/V OK, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1753 | 15 | 301754 | 04 |  | Hz/V OK, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 0 | 301755 | 04 |  | Ready for auto start, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 1 | 301755 | 04 |  | Ready for auto start, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 2 | 301755 | 04 |  | Ready for auto start, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 3 | 301755 | 04 |  | Ready for auto start, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 4 | 301755 | 04 |  | Ready for auto start, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 5 | 301755 | 04 |  | Ready for auto start, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 6 | 301755 | 04 |  | Ready for auto start, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 7 | 301755 | 04 |  | Ready for auto start, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 8 | 301755 | 04 |  | Ready for auto start, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 9 | 301755 | 04 |  | Ready for auto start, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 10 | 301755 | 04 |  | Ready for auto start, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 11 | 301755 | 04 |  | Ready for auto start, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 12 | 301755 | 04 |  | Ready for auto start, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 13 | 301755 | 04 |  | Ready for auto start, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 14 | 301755 | 04 |  | Ready for auto start, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1754 | 15 | 301755 | 04 |  | Ready for auto start, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 0 | 301756 | 04 |  | Running, ID 17 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 1 | 301756 | 04 |  | Running, ID 18 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 2 | 301756 | 04 |  | Running, ID 19 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 3 | 301756 | 04 |  | Running, ID 20 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 4 | 301756 | 04 |  | Running, ID 21 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 5 | 301756 | 04 |  | Running, ID 22 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 6 | 301756 | 04 |  | Running, ID 23 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 7 | 301756 | 04 |  | Running, ID 24 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 8 | 301756 | 04 |  | Running, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 9 | 301756 | 04 |  | Running, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 10 | 301756 | 04 |  | Running, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 11 | 301756 | 04 |  | Running, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 12 | 301756 | 04 |  | Running, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 13 | 301756 | 04 |  | Running, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 14 | 301756 | 04 |  | Running, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1755 | 15 | 301756 | 04 |  | Running, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 0 | 301757 | 04 |  | Dry Mode active on ID17 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 1 | 301757 | 04 |  | Dry Mode active on ID18 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 2 | 301757 | 04 |  | Dry Mode active on ID19 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 3 | 301757 | 04 |  | Dry Mode active on ID20 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 4 | 301757 | 04 |  | Dry Mode active on ID21 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 5 | 301757 | 04 |  | Dry Mode active on ID22 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 6 | 301757 | 04 |  | Dry Mode active on ID23 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 7 | 301757 | 04 |  | Dry Mode active on ID24 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 8 | 301757 | 04 |  | Dry Mode active on ID25 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 9 | 301757 | 04 |  | Dry Mode active on ID26 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 10 | 301757 | 04 |  | Dry Mode active on ID27 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 11 | 301757 | 04 |  | Dry Mode active on ID28 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 12 | 301757 | 04 |  | Dry Mode active on ID29 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 13 | 301757 | 04 |  | Dry Mode active on ID30 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 14 | 301757 | 04 |  | Dry Mode active on ID31 | BOOL |  |  |  | X | X
PM Plant logic state | 1756 | 15 | 301757 | 04 |  | Dry Mode active on ID32 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 0 | 301758 | 04 |  | MB pos. ON, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 1 | 301758 | 04 |  | MB pos. ON, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 2 | 301758 | 04 |  | MB pos. ON, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 3 | 301758 | 04 |  | MB pos. ON, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 4 | 301758 | 04 |  | MB pos. ON, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 5 | 301758 | 04 |  | MB pos. ON, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 6 | 301758 | 04 |  | MB pos. ON, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 7 | 301758 | 04 |  | MB pos. ON, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 8 | 301758 | 04 |  | MB pos. ON, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 9 | 301758 | 04 |  | MB pos. ON, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 10 | 301758 | 04 |  | MB pos. ON, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 11 | 301758 | 04 |  | MB pos. ON, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 12 | 301758 | 04 |  | MB pos. ON, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 13 | 301758 | 04 |  | MB pos. ON, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 14 | 301758 | 04 |  | MB pos. ON, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1757 | 15 | 301758 | 04 |  | MB pos. ON, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 0 | 301759 | 04 |  | MB pos. OFF, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 1 | 301759 | 04 |  | MB pos. OFF, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 2 | 301759 | 04 |  | MB pos. OFF, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 3 | 301759 | 04 |  | MB pos. OFF, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 4 | 301759 | 04 |  | MB pos. OFF, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 5 | 301759 | 04 |  | MB pos. OFF, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 6 | 301759 | 04 |  | MB pos. OFF, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 7 | 301759 | 04 |  | MB pos. OFF, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 8 | 301759 | 04 |  | MB pos. OFF, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 9 | 301759 | 04 |  | MB pos. OFF, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 10 | 301759 | 04 |  | MB pos. OFF, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 11 | 301759 | 04 |  | MB pos. OFF, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 12 | 301759 | 04 |  | MB pos. OFF, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 13 | 301759 | 04 |  | MB pos. OFF, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 14 | 301759 | 04 |  | MB pos. OFF, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1758 | 15 | 301759 | 04 |  | MB pos. OFF, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 0 | 301760 | 04 |  | MB synchronising, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 1 | 301760 | 04 |  | MB synchronising, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 2 | 301760 | 04 |  | MB synchronising, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 3 | 301760 | 04 |  | MB synchronising, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 4 | 301760 | 04 |  | MB synchronising, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 5 | 301760 | 04 |  | MB synchronising, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 6 | 301760 | 04 |  | MB synchronising, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 7 | 301760 | 04 |  | MB synchronising, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 8 | 301760 | 04 |  | MB synchronising, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 9 | 301760 | 04 |  | MB synchronising, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 10 | 301760 | 04 |  | MB synchronising, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 11 | 301760 | 04 |  | MB synchronising, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 12 | 301760 | 04 |  | MB synchronising, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 13 | 301760 | 04 |  | MB synchronising, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 14 | 301760 | 04 |  | MB synchronising, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1759 | 15 | 301760 | 04 |  | MB synchronising, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 0 | 301761 | 04 |  | TB pos. ON, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 1 | 301761 | 04 |  | TB pos. ON, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 2 | 301761 | 04 |  | TB pos. ON, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 3 | 301761 | 04 |  | TB pos. ON, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 4 | 301761 | 04 |  | TB pos. ON, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 5 | 301761 | 04 |  | TB pos. ON, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 6 | 301761 | 04 |  | TB pos. ON, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 7 | 301761 | 04 |  | TB pos. ON, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 8 | 301761 | 04 |  | TB pos. ON, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 9 | 301761 | 04 |  | TB pos. ON, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 10 | 301761 | 04 |  | TB pos. ON, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 11 | 301761 | 04 |  | TB pos. ON, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 12 | 301761 | 04 |  | TB pos. ON, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 13 | 301761 | 04 |  | TB pos. ON, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 14 | 301761 | 04 |  | TB pos. ON, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1760 | 15 | 301761 | 04 |  | TB pos. ON, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 0 | 301762 | 04 |  | TB pos. OFF, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 1 | 301762 | 04 |  | TB pos. OFF, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 2 | 301762 | 04 |  | TB pos. OFF, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 3 | 301762 | 04 |  | TB pos. OFF, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 4 | 301762 | 04 |  | TB pos. OFF, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 5 | 301762 | 04 |  | TB pos. OFF, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 6 | 301762 | 04 |  | TB pos. OFF, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 7 | 301762 | 04 |  | TB pos. OFF, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 8 | 301762 | 04 |  | TB pos. OFF, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 9 | 301762 | 04 |  | TB pos. OFF, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 10 | 301762 | 04 |  | TB pos. OFF, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 11 | 301762 | 04 |  | TB pos. OFF, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 12 | 301762 | 04 |  | TB pos. OFF, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 13 | 301762 | 04 |  | TB pos. OFF, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 14 | 301762 | 04 |  | TB pos. OFF, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1761 | 15 | 301762 | 04 |  | TB pos. OFF, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 0 | 301763 | 04 |  | TB synchronising, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 1 | 301763 | 04 |  | TB synchronising, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 2 | 301763 | 04 |  | TB synchronising, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 3 | 301763 | 04 |  | TB synchronising, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 4 | 301763 | 04 |  | TB synchronising, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 5 | 301763 | 04 |  | TB synchronising, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 6 | 301763 | 04 |  | TB synchronising, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 7 | 301763 | 04 |  | TB synchronising, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 8 | 301763 | 04 |  | TB synchronising, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 9 | 301763 | 04 |  | TB synchronising, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 10 | 301763 | 04 |  | TB synchronising, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 11 | 301763 | 04 |  | TB synchronising, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 12 | 301763 | 04 |  | TB synchronising, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 13 | 301763 | 04 |  | TB synchronising, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 14 | 301763 | 04 |  | TB synchronising, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1762 | 15 | 301763 | 04 |  | TB synchronising, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 0 | 301764 | 04 |  | Mains transducer-configured, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 1 | 301764 | 04 |  | Mains transducer-configured, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 2 | 301764 | 04 |  | Mains transducer-configured, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 3 | 301764 | 04 |  | Mains transducer-configured, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 4 | 301764 | 04 |  | Mains transducer-configured, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 5 | 301764 | 04 |  | Mains transducer-configured, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 6 | 301764 | 04 |  | Mains transducer-configured, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 7 | 301764 | 04 |  | Mains transducer-configured, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 8 | 301764 | 04 |  | Mains transducer-configured, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 9 | 301764 | 04 |  | Mains transducer-configured, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 10 | 301764 | 04 |  | Mains transducer-configured, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 11 | 301764 | 04 |  | Mains transducer-configured, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 12 | 301764 | 04 |  | Mains transducer-configured, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 13 | 301764 | 04 |  | Mains transducer-configured, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 14 | 301764 | 04 |  | Mains transducer-configured, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1763 | 15 | 301764 | 04 |  | Mains transducer-configured, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 0 | 301765 | 04 |  | TB transducer-configured, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 1 | 301765 | 04 |  | TB transducer-configured, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 2 | 301765 | 04 |  | TB transducer-configured, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 3 | 301765 | 04 |  | TB transducer-configured, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 4 | 301765 | 04 |  | TB transducer-configured, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 5 | 301765 | 04 |  | TB transducer-configured, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 6 | 301765 | 04 |  | TB transducer-configured, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 7 | 301765 | 04 |  | TB transducer-configured, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 8 | 301765 | 04 |  | TB transducer-configured, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 9 | 301765 | 04 |  | TB transducer-configured, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 10 | 301765 | 04 |  | TB transducer-configured, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 11 | 301765 | 04 |  | TB transducer-configured, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 12 | 301765 | 04 |  | TB transducer-configured, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 13 | 301765 | 04 |  | TB transducer-configured, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 14 | 301765 | 04 |  | TB transducer-configured, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1764 | 15 | 301765 | 04 |  | TB transducer-configured, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 0 | 301766 | 04 |  | Mains OK, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 1 | 301766 | 04 |  | Mains OK, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 2 | 301766 | 04 |  | Mains OK, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 3 | 301766 | 04 |  | Mains OK, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 4 | 301766 | 04 |  | Mains OK, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 5 | 301766 | 04 |  | Mains OK, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 6 | 301766 | 04 |  | Mains OK, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 7 | 301766 | 04 |  | Mains OK, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 8 | 301766 | 04 |  | Mains OK, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 9 | 301766 | 04 |  | Mains OK, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 10 | 301766 | 04 |  | Mains OK, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 11 | 301766 | 04 |  | Mains OK, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 12 | 301766 | 04 |  | Mains OK, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 13 | 301766 | 04 |  | Mains OK, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 14 | 301766 | 04 |  | Mains OK, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1765 | 15 | 301766 | 04 |  | Mains OK, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 0 | 301767 | 04 |  | Mains not in semi 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 1 | 301767 | 04 |  | Mains not in semi 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 2 | 301767 | 04 |  | Mains not in semi 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 3 | 301767 | 04 |  | Mains not in semi 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 4 | 301767 | 04 |  | Mains not in semi 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 5 | 301767 | 04 |  | Mains not in semi 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 6 | 301767 | 04 |  | Mains not in semi 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 7 | 301767 | 04 |  | Mains not in semi 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 8 | 301767 | 04 |  | Mains not in semi 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 9 | 301767 | 04 |  | Mains not in semi 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 10 | 301767 | 04 |  | Mains not in semi 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 11 | 301767 | 04 |  | Mains not in semi 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 12 | 301767 | 04 |  | Mains not in semi 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 13 | 301767 | 04 |  | Mains not in semi 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 14 | 301767 | 04 |  | Mains not in semi 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1766 | 15 | 301767 | 04 |  | Mains not in semi 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 0 | 301768 | 04 |  | Mains failure, ID 1 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 1 | 301768 | 04 |  | Mains failure, ID 2 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 2 | 301768 | 04 |  | Mains failure, ID 3 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 3 | 301768 | 04 |  | Mains failure, ID 4 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 4 | 301768 | 04 |  | Mains failure, ID 5 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 5 | 301768 | 04 |  | Mains failure, ID 6 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 6 | 301768 | 04 |  | Mains failure, ID 7 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 7 | 301768 | 04 |  | Mains failure, ID 8 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 8 | 301768 | 04 |  | Mains failure, ID 9 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 9 | 301768 | 04 |  | Mains failure, ID 10 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 10 | 301768 | 04 |  | Mains failure, ID 11 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 11 | 301768 | 04 |  | Mains failure, ID 12 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 12 | 301768 | 04 |  | Mains failure, ID 13 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 13 | 301768 | 04 |  | Mains failure, ID 14 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 14 | 301768 | 04 |  | Mains failure, ID 15 | BOOL |  |  |  | X | X
PM Plant logic state | 1767 | 15 | 301768 | 04 |  | Mains failure, ID 16 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 0 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 1 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 2 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 3 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 4 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 5 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 6 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 7 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 8 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 9 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 10 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 11 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 12 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 13 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 14 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1771 | 15 | 301772 | 04 |  | PV running / Any LG breaker closed, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 0 | 301773 | 04 |  | Ready to autostart, ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 1 | 301773 | 04 |  | Ready to autostart, ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 2 | 301773 | 04 |  | Ready to autostart, ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 3 | 301773 | 04 |  | Ready to autostart, ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 4 | 301773 | 04 |  | Ready to autostart, ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 5 | 301773 | 04 |  | Ready to autostart, ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 6 | 301773 | 04 |  | Ready to autostart, ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 7 | 301773 | 04 |  | Ready to autostart, ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 8 | 301773 | 04 |  | Ready to autostart, ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 9 | 301773 | 04 |  | Ready to autostart, ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 10 | 301773 | 04 |  | Ready to autostart, ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 11 | 301773 | 04 |  | Ready to autostart, ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 12 | 301773 | 04 |  | Ready to autostart, ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 13 | 301773 | 04 |  | Ready to autostart, ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 14 | 301773 | 04 |  | Ready to autostart, ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1772 | 15 | 301773 | 04 |  | Ready to autostart, ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 0 | 301774 | 04 |  | Load Group 1 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 1 | 301774 | 04 |  | Load Group 1 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 2 | 301774 | 04 |  | Load Group 1 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 3 | 301774 | 04 |  | Load Group 1 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 4 | 301774 | 04 |  | Load Group 1 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 5 | 301774 | 04 |  | Load Group 1 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 6 | 301774 | 04 |  | Load Group 1 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 7 | 301774 | 04 |  | Load Group 1 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 8 | 301774 | 04 |  | Load Group 1 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 9 | 301774 | 04 |  | Load Group 1 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 10 | 301774 | 04 |  | Load Group 1 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 11 | 301774 | 04 |  | Load Group 1 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 12 | 301774 | 04 |  | Load Group 1 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 13 | 301774 | 04 |  | Load Group 1 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 14 | 301774 | 04 |  | Load Group 1 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1773 | 15 | 301774 | 04 |  | Load Group 1 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 0 | 301775 | 04 |  | Load Group 2 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 1 | 301775 | 04 |  | Load Group 2 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 2 | 301775 | 04 |  | Load Group 2 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 3 | 301775 | 04 |  | Load Group 2 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 4 | 301775 | 04 |  | Load Group 2 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 5 | 301775 | 04 |  | Load Group 2 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 6 | 301775 | 04 |  | Load Group 2 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 7 | 301775 | 04 |  | Load Group 2 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 8 | 301775 | 04 |  | Load Group 2 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 9 | 301775 | 04 |  | Load Group 2 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 10 | 301775 | 04 |  | Load Group 2 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 11 | 301775 | 04 |  | Load Group 2 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 12 | 301775 | 04 |  | Load Group 2 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 13 | 301775 | 04 |  | Load Group 2 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 14 | 301775 | 04 |  | Load Group 2 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1774 | 15 | 301775 | 04 |  | Load Group 2 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 0 | 301776 | 04 |  | Load Group 3 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 1 | 301776 | 04 |  | Load Group 3 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 2 | 301776 | 04 |  | Load Group 3 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 3 | 301776 | 04 |  | Load Group 3 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 4 | 301776 | 04 |  | Load Group 3 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 5 | 301776 | 04 |  | Load Group 3 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 6 | 301776 | 04 |  | Load Group 3 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 7 | 301776 | 04 |  | Load Group 3 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 8 | 301776 | 04 |  | Load Group 3 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 9 | 301776 | 04 |  | Load Group 3 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 10 | 301776 | 04 |  | Load Group 3 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 11 | 301776 | 04 |  | Load Group 3 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 12 | 301776 | 04 |  | Load Group 3 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 13 | 301776 | 04 |  | Load Group 3 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 14 | 301776 | 04 |  | Load Group 3 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1775 | 15 | 301776 | 04 |  | Load Group 3 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 0 | 301777 | 04 |  | Load Group 4 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 1 | 301777 | 04 |  | Load Group 4 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 2 | 301777 | 04 |  | Load Group 4 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 3 | 301777 | 04 |  | Load Group 4 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 4 | 301777 | 04 |  | Load Group 4 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 5 | 301777 | 04 |  | Load Group 4 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 6 | 301777 | 04 |  | Load Group 4 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 7 | 301777 | 04 |  | Load Group 4 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 8 | 301777 | 04 |  | Load Group 4 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 9 | 301777 | 04 |  | Load Group 4 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 10 | 301777 | 04 |  | Load Group 4 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 11 | 301777 | 04 |  | Load Group 4 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 12 | 301777 | 04 |  | Load Group 4 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 13 | 301777 | 04 |  | Load Group 4 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 14 | 301777 | 04 |  | Load Group 4 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1776 | 15 | 301777 | 04 |  | Load Group 4 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 0 | 301778 | 04 |  | Load Group 5 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 1 | 301778 | 04 |  | Load Group 5 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 2 | 301778 | 04 |  | Load Group 5 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 3 | 301778 | 04 |  | Load Group 5 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 4 | 301778 | 04 |  | Load Group 5 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 5 | 301778 | 04 |  | Load Group 5 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 6 | 301778 | 04 |  | Load Group 5 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 7 | 301778 | 04 |  | Load Group 5 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 8 | 301778 | 04 |  | Load Group 5 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 9 | 301778 | 04 |  | Load Group 5 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 10 | 301778 | 04 |  | Load Group 5 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 11 | 301778 | 04 |  | Load Group 5 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 12 | 301778 | 04 |  | Load Group 5 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 13 | 301778 | 04 |  | Load Group 5 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 14 | 301778 | 04 |  | Load Group 5 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1777 | 15 | 301778 | 04 |  | Load Group 5 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 0 | 301779 | 04 |  | Load Group 6 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 1 | 301779 | 04 |  | Load Group 6 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 2 | 301779 | 04 |  | Load Group 6 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 3 | 301779 | 04 |  | Load Group 6 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 4 | 301779 | 04 |  | Load Group 6 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 5 | 301779 | 04 |  | Load Group 6 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 6 | 301779 | 04 |  | Load Group 6 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 7 | 301779 | 04 |  | Load Group 6 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 8 | 301779 | 04 |  | Load Group 6 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 9 | 301779 | 04 |  | Load Group 6 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 10 | 301779 | 04 |  | Load Group 6 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 11 | 301779 | 04 |  | Load Group 6 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 12 | 301779 | 04 |  | Load Group 6 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 13 | 301779 | 04 |  | Load Group 6 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 14 | 301779 | 04 |  | Load Group 6 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1778 | 15 | 301779 | 04 |  | Load Group 6 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 0 | 301780 | 04 |  | Load Group 7 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 1 | 301780 | 04 |  | Load Group 7 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 2 | 301780 | 04 |  | Load Group 7 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 3 | 301780 | 04 |  | Load Group 7 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 4 | 301780 | 04 |  | Load Group 7 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 5 | 301780 | 04 |  | Load Group 7 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 6 | 301780 | 04 |  | Load Group 7 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 7 | 301780 | 04 |  | Load Group 7 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 8 | 301780 | 04 |  | Load Group 7 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 9 | 301780 | 04 |  | Load Group 7 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 10 | 301780 | 04 |  | Load Group 7 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 11 | 301780 | 04 |  | Load Group 7 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 12 | 301780 | 04 |  | Load Group 7 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 13 | 301780 | 04 |  | Load Group 7 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 14 | 301780 | 04 |  | Load Group 7 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1779 | 15 | 301780 | 04 |  | Load Group 7 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 0 | 301781 | 04 |  | Load Group 8 Pos ON - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 1 | 301781 | 04 |  | Load Group 8 Pos ON - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 2 | 301781 | 04 |  | Load Group 8 Pos ON - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 3 | 301781 | 04 |  | Load Group 8 Pos ON - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 4 | 301781 | 04 |  | Load Group 8 Pos ON - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 5 | 301781 | 04 |  | Load Group 8 Pos ON - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 6 | 301781 | 04 |  | Load Group 8 Pos ON - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 7 | 301781 | 04 |  | Load Group 8 Pos ON - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 8 | 301781 | 04 |  | Load Group 8 Pos ON - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 9 | 301781 | 04 |  | Load Group 8 Pos ON - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 10 | 301781 | 04 |  | Load Group 8 Pos ON - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 11 | 301781 | 04 |  | Load Group 8 Pos ON - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 12 | 301781 | 04 |  | Load Group 8 Pos ON - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 13 | 301781 | 04 |  | Load Group 8 Pos ON - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 14 | 301781 | 04 |  | Load Group 8 Pos ON - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1780 | 15 | 301781 | 04 |  | Load Group 8 Pos ON - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 0 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 1 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 2 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 3 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 4 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 5 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 6 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 7 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 8 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 9 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 10 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 11 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 12 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 13 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 14 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1781 | 15 | 301782 | 04 |  | Load Group 1 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 0 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 1 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 2 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 3 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 4 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 5 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 6 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 7 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 8 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 9 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 10 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 11 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 12 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 13 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 14 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1782 | 15 | 301783 | 04 |  | Load Group 2 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 0 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 1 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 2 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 3 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 4 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 5 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 6 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 7 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 8 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 9 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 10 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 11 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 12 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 13 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 14 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1783 | 15 | 301784 | 04 |  | Load Group 3 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 0 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 1 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 2 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 3 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 4 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 5 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 6 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 7 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 8 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 9 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 10 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 11 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 12 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 13 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 14 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1784 | 15 | 301785 | 04 |  | Load Group 4 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 0 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 1 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 2 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 3 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 4 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 5 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 6 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 7 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 8 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 9 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 10 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 11 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 12 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 13 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 14 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1785 | 15 | 301786 | 04 |  | Load Group 5 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 0 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 1 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 2 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 3 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 4 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 5 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 6 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 7 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 8 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 9 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 10 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 11 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 12 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 13 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 14 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1786 | 15 | 301787 | 04 |  | Load Group 6 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 0 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 1 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 2 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 3 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 4 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 5 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 6 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 7 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 8 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 9 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 10 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 11 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 12 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 13 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 14 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1787 | 15 | 301788 | 04 |  | Load Group 7 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 0 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 1 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 2 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 3 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 4 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 5 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 6 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 7 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 8 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 9 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 10 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 11 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 12 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 13 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 14 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1788 | 15 | 301789 | 04 |  | Load Group 8 Pos OFF - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 0 | 301790 | 04 |  | Load Group 1 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 1 | 301790 | 04 |  | Load Group 1 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 2 | 301790 | 04 |  | Load Group 1 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 3 | 301790 | 04 |  | Load Group 1 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 4 | 301790 | 04 |  | Load Group 1 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 5 | 301790 | 04 |  | Load Group 1 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 6 | 301790 | 04 |  | Load Group 1 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 7 | 301790 | 04 |  | Load Group 1 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 8 | 301790 | 04 |  | Load Group 1 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 9 | 301790 | 04 |  | Load Group 1 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 10 | 301790 | 04 |  | Load Group 1 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 11 | 301790 | 04 |  | Load Group 1 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 12 | 301790 | 04 |  | Load Group 1 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 13 | 301790 | 04 |  | Load Group 1 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 14 | 301790 | 04 |  | Load Group 1 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1789 | 15 | 301790 | 04 |  | Load Group 1 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 0 | 301791 | 04 |  | Load Group 2 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 1 | 301791 | 04 |  | Load Group 2 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 2 | 301791 | 04 |  | Load Group 2 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 3 | 301791 | 04 |  | Load Group 2 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 4 | 301791 | 04 |  | Load Group 2 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 5 | 301791 | 04 |  | Load Group 2 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 6 | 301791 | 04 |  | Load Group 2 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 7 | 301791 | 04 |  | Load Group 2 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 8 | 301791 | 04 |  | Load Group 2 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 9 | 301791 | 04 |  | Load Group 2 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 10 | 301791 | 04 |  | Load Group 2 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 11 | 301791 | 04 |  | Load Group 2 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 12 | 301791 | 04 |  | Load Group 2 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 13 | 301791 | 04 |  | Load Group 2 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 14 | 301791 | 04 |  | Load Group 2 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1790 | 15 | 301791 | 04 |  | Load Group 2 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 0 | 301792 | 04 |  | Load Group 3 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 1 | 301792 | 04 |  | Load Group 3 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 2 | 301792 | 04 |  | Load Group 3 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 3 | 301792 | 04 |  | Load Group 3 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 4 | 301792 | 04 |  | Load Group 3 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 5 | 301792 | 04 |  | Load Group 3 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 6 | 301792 | 04 |  | Load Group 3 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 7 | 301792 | 04 |  | Load Group 3 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 8 | 301792 | 04 |  | Load Group 3 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 9 | 301792 | 04 |  | Load Group 3 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 10 | 301792 | 04 |  | Load Group 3 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 11 | 301792 | 04 |  | Load Group 3 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 12 | 301792 | 04 |  | Load Group 3 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 13 | 301792 | 04 |  | Load Group 3 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 14 | 301792 | 04 |  | Load Group 3 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1791 | 15 | 301792 | 04 |  | Load Group 3 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 0 | 301793 | 04 |  | Load Group 4 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 1 | 301793 | 04 |  | Load Group 4 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 2 | 301793 | 04 |  | Load Group 4 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 3 | 301793 | 04 |  | Load Group 4 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 4 | 301793 | 04 |  | Load Group 4 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 5 | 301793 | 04 |  | Load Group 4 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 6 | 301793 | 04 |  | Load Group 4 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 7 | 301793 | 04 |  | Load Group 4 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 8 | 301793 | 04 |  | Load Group 4 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 9 | 301793 | 04 |  | Load Group 4 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 10 | 301793 | 04 |  | Load Group 4 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 11 | 301793 | 04 |  | Load Group 4 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 12 | 301793 | 04 |  | Load Group 4 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 13 | 301793 | 04 |  | Load Group 4 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 14 | 301793 | 04 |  | Load Group 4 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1792 | 15 | 301793 | 04 |  | Load Group 4 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 0 | 301794 | 04 |  | Load Group 5 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 1 | 301794 | 04 |  | Load Group 5 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 2 | 301794 | 04 |  | Load Group 5 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 3 | 301794 | 04 |  | Load Group 5 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 4 | 301794 | 04 |  | Load Group 5 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 5 | 301794 | 04 |  | Load Group 5 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 6 | 301794 | 04 |  | Load Group 5 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 7 | 301794 | 04 |  | Load Group 5 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 8 | 301794 | 04 |  | Load Group 5 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 9 | 301794 | 04 |  | Load Group 5 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 10 | 301794 | 04 |  | Load Group 5 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 11 | 301794 | 04 |  | Load Group 5 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 12 | 301794 | 04 |  | Load Group 5 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 13 | 301794 | 04 |  | Load Group 5 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 14 | 301794 | 04 |  | Load Group 5 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1793 | 15 | 301794 | 04 |  | Load Group 5 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 0 | 301795 | 04 |  | Load Group 6 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 1 | 301795 | 04 |  | Load Group 6 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 2 | 301795 | 04 |  | Load Group 6 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 3 | 301795 | 04 |  | Load Group 6 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 4 | 301795 | 04 |  | Load Group 6 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 5 | 301795 | 04 |  | Load Group 6 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 6 | 301795 | 04 |  | Load Group 6 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 7 | 301795 | 04 |  | Load Group 6 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 8 | 301795 | 04 |  | Load Group 6 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 9 | 301795 | 04 |  | Load Group 6 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 10 | 301795 | 04 |  | Load Group 6 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 11 | 301795 | 04 |  | Load Group 6 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 12 | 301795 | 04 |  | Load Group 6 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 13 | 301795 | 04 |  | Load Group 6 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 14 | 301795 | 04 |  | Load Group 6 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1794 | 15 | 301795 | 04 |  | Load Group 6 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 0 | 301796 | 04 |  | Load Group 7 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 1 | 301796 | 04 |  | Load Group 7 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 2 | 301796 | 04 |  | Load Group 7 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 3 | 301796 | 04 |  | Load Group 7 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 4 | 301796 | 04 |  | Load Group 7 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 5 | 301796 | 04 |  | Load Group 7 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 6 | 301796 | 04 |  | Load Group 7 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 7 | 301796 | 04 |  | Load Group 7 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 8 | 301796 | 04 |  | Load Group 7 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 9 | 301796 | 04 |  | Load Group 7 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 10 | 301796 | 04 |  | Load Group 7 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 11 | 301796 | 04 |  | Load Group 7 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 12 | 301796 | 04 |  | Load Group 7 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 13 | 301796 | 04 |  | Load Group 7 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 14 | 301796 | 04 |  | Load Group 7 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1795 | 15 | 301796 | 04 |  | Load Group 7 Enabled - ID 32 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 0 | 301797 | 04 |  | Load Group 8 Enabled - ID 33 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 1 | 301797 | 04 |  | Load Group 8 Enabled - ID 34 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 2 | 301797 | 04 |  | Load Group 8 Enabled - ID 35 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 3 | 301797 | 04 |  | Load Group 8 Enabled - ID 36 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 4 | 301797 | 04 |  | Load Group 8 Enabled - ID 37 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 5 | 301797 | 04 |  | Load Group 8 Enabled - ID 38 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 6 | 301797 | 04 |  | Load Group 8 Enabled - ID 39 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 7 | 301797 | 04 |  | Load Group 8 Enabled - ID 40 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 8 | 301797 | 04 |  | Load Group 8 Enabled - ID 25 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 9 | 301797 | 04 |  | Load Group 8 Enabled - ID 26 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 10 | 301797 | 04 |  | Load Group 8 Enabled - ID 27 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 11 | 301797 | 04 |  | Load Group 8 Enabled - ID 28 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 12 | 301797 | 04 |  | Load Group 8 Enabled - ID 29 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 13 | 301797 | 04 |  | Load Group 8 Enabled - ID 30 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 14 | 301797 | 04 |  | Load Group 8 Enabled - ID 31 | BOOL |  |  |  | X | X
PM Plant logic state | 1796 | 15 | 301797 | 04 |  | Load Group 8 Enabled - ID 32 | BOOL |  |  |  | X | X
PV monitoring area | 40000 |  | 340001 | 04 |  | DC voltage string 05 | INT16u | AB | 1 | V | X
PV monitoring area | 40001 |  | 340002 | 04 |  | DC power string 05 | INT16s | AB | 1 | kW | X
PV monitoring area | 40002 |  | 340003 | 04 |  | DC voltage string 06 | INT16u | AB | 1 | V | X
PV monitoring area | 40003 |  | 340004 | 04 |  | DC power string 06 | INT16s | AB | 1 | kW | X
PV monitoring area | 40004 |  | 340005 | 04 |  | DC voltage string 07 | INT16u | AB | 1 | V | X
PV monitoring area | 40005 |  | 340006 | 04 |  | DC power string 07 | INT16s | AB | 1 | kW | X
PV monitoring area | 40006 |  | 340007 | 04 |  | DC voltage string 08 | INT16u | AB | 1 | V | X
PV monitoring area | 40007 |  | 340008 | 04 |  | DC power string 08 | INT16s | AB | 1 | kW | X
PV monitoring area | 40008 |  | 340009 | 04 |  | DC voltage string 09 | INT16u | AB | 1 | V | X
PV monitoring area | 40009 |  | 340010 | 04 |  | DC power string 09 | INT16s | AB | 1 | kW | X
PV monitoring area | 40010 |  | 340011 | 04 |  | DC voltage string 10 | INT16u | AB | 1 | V | X
PV monitoring area | 40011 |  | 340012 | 04 |  | DC power string 10 | INT16s | AB | 1 | kW | X
PV monitoring area | 40012 |  | 340013 | 04 |  | DC voltage string 11 | INT16u | AB | 1 | V | X
PV monitoring area | 40013 |  | 340014 | 04 |  | DC power string 11 | INT16s | AB | 1 | kW | X
PV monitoring area | 40014 |  | 340015 | 04 |  | DC voltage string 12 | INT16u | AB | 1 | V | X
PV monitoring area | 40015 |  | 340016 | 04 |  | DC power string 12 | INT16s | AB | 1 | kW | X
PV monitoring area | 40016 |  | 340017 | 04 |  | DC current string 01 | INT16u | AB | 1 | A | X
PV monitoring area | 40017 |  | 340018 | 04 |  | DC current string 02 | INT16u | AB | 1 | A | X
PV monitoring area | 40018 |  | 340019 | 04 |  | DC current string 03 | INT16u | AB | 1 | A | X
PV monitoring area | 40019 |  | 340020 | 04 |  | DC current string 04 | INT16u | AB | 1 | A | X
PV monitoring area | 40020 |  | 340021 | 04 |  | DC current string 05 | INT16u | AB | 1 | A | X
PV monitoring area | 40021 |  | 340022 | 04 |  | DC current string 06 | INT16u | AB | 1 | A | X
PV monitoring area | 40022 |  | 340023 | 04 |  | DC current string 07 | INT16u | AB | 1 | A | X
PV monitoring area | 40023 |  | 340024 | 04 |  | DC current string 08 | INT16u | AB | 1 | A | X
PV monitoring area | 40024 |  | 340025 | 04 |  | DC current string 09 | INT16u | AB | 1 | A | X
PV monitoring area | 40025 |  | 340026 | 04 |  | DC current string 10 | INT16u | AB | 1 | A | X
PV monitoring area | 40026 |  | 340027 | 04 |  | DC current string 11 | INT16u | AB | 1 | A | X
PV monitoring area | 40027 |  | 340028 | 04 |  | DC current string 12 | INT16u | AB | 1 | A | X
PV monitoring area | 40028 |  | 340029 | 04 |  | DC current string 13 | INT16u | AB | 1 | A | X
PV monitoring area | 40029 |  | 340030 | 04 |  | DC current string 14 | INT16u | AB | 1 | A | X
PV monitoring area | 40030 |  | 340031 | 04 |  | DC current string 15 | INT16u | AB | 1 | A | X
PV monitoring area | 40031 |  | 340032 | 04 |  | DC current string 16 | INT16u | AB | 1 | A | X
PV monitoring area | 40032 |  | 340033 | 04 |  | DC current string 17 | INT16u | AB | 1 | A | X
PV monitoring area | 40033 |  | 340034 | 04 |  | DC current string 18 | INT16u | AB | 1 | A | X
PV monitoring area | 40034 |  | 340035 | 04 |  | DC current string 19 | INT16u | AB | 1 | A | X
PV monitoring area | 40035 |  | 340036 | 04 |  | DC current string 20 | INT16u | AB | 1 | A | X
PV monitoring area | 40036 |  | 340037 | 04 |  | DC current string 21 | INT16u | AB | 1 | A | X
PV monitoring area | 40037 |  | 340038 | 04 |  | DC current string 22 | INT16u | AB | 1 | A | X
PV monitoring area | 40038 |  | 340039 | 04 |  | DC current string 23 | INT16u | AB | 1 | A | X
PV monitoring area | 40039 |  | 340040 | 04 |  | DC current string 24 | INT16u | AB | 1 | A | X
Forecast area 1 | 44000 |  | 344001 | 04 |  | Time stamp of when forecast applies | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44002 |  | 344003 | 04 |  | Mean forecast (equals P50) | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44004 |  | 344005 | 04 |  | Minimum forecast (equals P10) | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44006 |  | 344007 | 04 |  | Maximum forecast (equals P90) | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44008 |  | 344009 | 04 |  | P10 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44010 |  | 344011 | 04 |  | P20 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44012 |  | 344013 | 04 |  | P30 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44014 |  | 344015 | 04 |  | P40 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44016 |  | 344017 | 04 |  | P50 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44018 |  | 344019 | 04 |  | P60 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44020 |  | 344021 | 04 |  | P70 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44022 |  | 344023 | 04 |  | P80 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 1 | 44024 |  | 344025 | 04 |  | P90 forecast | INT32s | ABCD | 0 |  | X | X
Forecast area 2 | 45560 |  | 345561 | 04 |  | 45560-45619: Forecast in power for the time horizon selected if time horizon of 20 minutes used for example only the Step1 to Step20 are updated. | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45620 |  | 345621 | 04 |  | Lowest forecast within the Start time horizon | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45621 |  | 345622 | 04 |  | Step number for Forecast start | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45622 |  | 345623 | 04 |  | Lowest forecast within the Stop time horizon | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45623 |  | 345624 | 04 |  | Step number for Forecast stop | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45624 |  | 345625 | 04 |  | 0: Start forecast active. 1: Stop forecast active. | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45625 |  | 345626 | 04 |  | Spinning reserve generated | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45626 |  | 345627 | 04 |  | 0: Communication inactive. 1: Communication inactive. | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45627 |  | 345628 | 04 |  | 0: Off. 1: SteadySun SteadyEye. | INT16s | AB | 0 |  | X | X
Forecast area 2 | 45628 |  | 345629 | 04 |  | Protocol selection. Characters 01-02. | string | AB | 0 |  | X | X
Forecast area 2 | 45629 |  | 345630 | 04 |  | Protocol selection. Characters 03-04. | string | AB | 0 |  | X | X
Forecast area 2 | 45630 |  | 345631 | 04 |  | Protocol selection. Characters 05-06. | string | AB | 0 |  | X | X
Forecast area 2 | 45631 |  | 345632 | 04 |  | Protocol selection. Characters 07-08. | string | AB | 0 |  | X | X
Forecast area 2 | 45632 |  | 345633 | 04 |  | Protocol selection. Characters 09-10. | string | AB | 0 |  | X | X
Forecast area 2 | 45633 |  | 345634 | 04 |  | Protocol selection. Characters 11-12. | string | AB | 0 |  | X | X
Forecast area 2 | 45634 |  | 345635 | 04 |  | Protocol selection. Characters 13-14. | string | AB | 0 |  | X | X
Forecast area 2 | 45635 |  | 345636 | 04 |  | Protocol selection. Characters 15-16. | string | AB | 0 |  | X | X
Forecast area 2 | 45636 |  | 345637 | 04 |  | Protocol selection. Characters 17-18. | string | AB | 0 |  | X | X
Forecast area 2 | 45637 |  | 345638 | 04 |  | Protocol selection. Characters 19-20. | string | AB | 0 |  | X | X
Power meter area 1 | 46000 |  | 346001 | 04 |  | DG 01 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46001 |  | 346002 | 04 |  | DG 02 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46002 |  | 346003 | 04 |  | DG 03 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46003 |  | 346004 | 04 |  | DG 04 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46004 |  | 346005 | 04 |  | DG 05 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46005 |  | 346006 | 04 |  | DG 06 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46006 |  | 346007 | 04 |  | DG 07 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46007 |  | 346008 | 04 |  | DG 08 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46008 |  | 346009 | 04 |  | DG 09 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46009 |  | 346010 | 04 |  | DG 10 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46010 |  | 346011 | 04 |  | DG 11 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46011 |  | 346012 | 04 |  | DG 12 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46012 |  | 346013 | 04 |  | DG 13 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46013 |  | 346014 | 04 |  | DG 14 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46014 |  | 346015 | 04 |  | DG 15 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46015 |  | 346016 | 04 |  | DG 16 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46016 |  | 346017 | 04 |  | DG 01 actual Q measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46017 |  | 346018 | 04 |  | DG 02 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46018 |  | 346019 | 04 |  | DG 03 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46019 |  | 346020 | 04 |  | DG 04 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46020 |  | 346021 | 04 |  | DG 05 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46021 |  | 346022 | 04 |  | DG 06 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46022 |  | 346023 | 04 |  | DG 07 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46023 |  | 346024 | 04 |  | DG 08 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46024 |  | 346025 | 04 |  | DG 09 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46025 |  | 346026 | 04 |  | DG 10 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46026 |  | 346027 | 04 |  | DG 11 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46027 |  | 346028 | 04 |  | DG 12 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46028 |  | 346029 | 04 |  | DG 13 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46029 |  | 346030 | 04 |  | DG 14 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46030 |  | 346031 | 04 |  | DG 15 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46031 |  | 346032 | 04 |  | DG 16 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46032 |  | 346033 | 04 |  | DG 01 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46033 |  | 346034 | 04 |  | DG 02 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46034 |  | 346035 | 04 |  | DG 03 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46035 |  | 346036 | 04 |  | DG 04 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46036 |  | 346037 | 04 |  | DG 05 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46037 |  | 346038 | 04 |  | DG 06 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46038 |  | 346039 | 04 |  | DG 07 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46039 |  | 346040 | 04 |  | DG 08 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46040 |  | 346041 | 04 |  | DG 09 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46041 |  | 346042 | 04 |  | DG 10 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46042 |  | 346043 | 04 |  | DG 11 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46043 |  | 346044 | 04 |  | DG 12 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46044 |  | 346045 | 04 |  | DG 13 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46045 |  | 346046 | 04 |  | DG 14 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46046 |  | 346047 | 04 |  | DG 15 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46047 |  | 346048 | 04 |  | DG 16 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46048 |  | 346049 | 04 |  | Is the communication to DG 01 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46049 |  | 346050 | 04 |  | Is the communication to DG 02 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46050 |  | 346051 | 04 |  | Is the communication to DG 03 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46051 |  | 346052 | 04 |  | Is the communication to DG 04 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46052 |  | 346053 | 04 |  | Is the communication to DG 05 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46053 |  | 346054 | 04 |  | Is the communication to DG 06 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46054 |  | 346055 | 04 |  | Is the communication to DG 07 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46055 |  | 346056 | 04 |  | Is the communication to DG 08 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46056 |  | 346057 | 04 |  | Is the communication to DG 09 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46057 |  | 346058 | 04 |  | Is the communication to DG 10 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46058 |  | 346059 | 04 |  | Is the communication to DG 11 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46059 |  | 346060 | 04 |  | Is the communication to DG 12 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46060 |  | 346061 | 04 |  | Is the communication to DG 13 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46061 |  | 346062 | 04 |  | Is the communication to DG 14 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46062 |  | 346063 | 04 |  | Is the communication to DG 15 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46063 |  | 346064 | 04 |  | Is the communication to DG 16 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46064 |  | 346065 | 04 |  | PV/ESS 01 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46065 |  | 346066 | 04 |  | PV/ESS 02 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46066 |  | 346067 | 04 |  | PV/ESS 03 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46067 |  | 346068 | 04 |  | PV/ESS 04 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46068 |  | 346069 | 04 |  | PV/ESS 05 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46069 |  | 346070 | 04 |  | PV/ESS 06 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46070 |  | 346071 | 04 |  | PV/ESS 07 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46071 |  | 346072 | 04 |  | PV/ESS 08 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46072 |  | 346073 | 04 |  | PV/ESS 09 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46073 |  | 346074 | 04 |  | PV/ESS 10 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46074 |  | 346075 | 04 |  | PV/ESS 11 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46075 |  | 346076 | 04 |  | PV/ESS 12 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46076 |  | 346077 | 04 |  | PV/ESS 13 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46077 |  | 346078 | 04 |  | PV/ESS 14 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46078 |  | 346079 | 04 |  | PV/ESS 15 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46079 |  | 346080 | 04 |  | PV/ESS 16 actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46080 |  | 346081 | 04 |  | PV/ESS 01 actual Q measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46081 |  | 346082 | 04 |  | PV/ESS 02 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46082 |  | 346083 | 04 |  | PV/ESS 03 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46083 |  | 346084 | 04 |  | PV/ESS 04 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46084 |  | 346085 | 04 |  | PV/ESS 05 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46085 |  | 346086 | 04 |  | PV/ESS 06 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46086 |  | 346087 | 04 |  | PV/ESS 07 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46087 |  | 346088 | 04 |  | PV/ESS 08 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46088 |  | 346089 | 04 |  | PV/ESS 09 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46089 |  | 346090 | 04 |  | PV/ESS 10 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46090 |  | 346091 | 04 |  | PV/ESS 11 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46091 |  | 346092 | 04 |  | PV/ESS 12 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46092 |  | 346093 | 04 |  | PV/ESS 13 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46093 |  | 346094 | 04 |  | PV/ESS 14 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46094 |  | 346095 | 04 |  | PV/ESS 15 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46095 |  | 346096 | 04 |  | PV/ESS 16 actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46096 |  | 346097 | 04 |  | PV/ESS 01 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46097 |  | 346098 | 04 |  | PV/ESS 02 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46098 |  | 346099 | 04 |  | PV/ESS 03 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46099 |  | 346100 | 04 |  | PV/ESS 04 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46100 |  | 346101 | 04 |  | PV/ESS 05 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46101 |  | 346102 | 04 |  | PV/ESS 06 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46102 |  | 346103 | 04 |  | PV/ESS 07 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46103 |  | 346104 | 04 |  | PV/ESS 08 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46104 |  | 346105 | 04 |  | PV/ESS 09 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46105 |  | 346106 | 04 |  | PV/ESS 10 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46106 |  | 346107 | 04 |  | PV/ESS 11 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46107 |  | 346108 | 04 |  | PV/ESS 12 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46108 |  | 346109 | 04 |  | PV/ESS 13 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46109 |  | 346110 | 04 |  | PV/ESS 14 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46110 |  | 346111 | 04 |  | PV/ESS 15 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46111 |  | 346112 | 04 |  | PV/ESS 16 power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46112 |  | 346113 | 04 |  | Is the communication to PV/ESS 01 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46113 |  | 346114 | 04 |  | Is the communication to PV/ESS 02 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46114 |  | 346115 | 04 |  | Is the communication to PV/ESS 03 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46115 |  | 346116 | 04 |  | Is the communication to PV/ESS 04 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46116 |  | 346117 | 04 |  | Is the communication to PV/ESS 05 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46117 |  | 346118 | 04 |  | Is the communication to PV/ESS 06 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46118 |  | 346119 | 04 |  | Is the communication to PV/ESS 07 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46119 |  | 346120 | 04 |  | Is the communication to PV/ESS 08 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46120 |  | 346121 | 04 |  | Is the communication to PV/ESS 09 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46121 |  | 346122 | 04 |  | Is the communication to PV/ESS 10 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46122 |  | 346123 | 04 |  | Is the communication to PV/ESS 11 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46123 |  | 346124 | 04 |  | Is the communication to PV/ESS 12 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46124 |  | 346125 | 04 |  | Is the communication to PV/ESS 13 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46125 |  | 346126 | 04 |  | Is the communication to PV/ESS 14 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46126 |  | 346127 | 04 |  | Is the communication to PV/ESS 15 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46127 |  | 346128 | 04 |  | Is the communication to PV/ESS 16 power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
Power meter area 1 | 46128 |  | 346129 | 04 |  | Mains actual P measurement from power meter reading | INT16s | AB | 0 | kW | X | X
Power meter area 1 | 46129 |  | 346130 | 04 |  | Mains actual Q measurement from power meter reading | INT16s | AB | 0 | kvar | X | X
Power meter area 1 | 46130 |  | 346131 | 04 |  | Mains power meter digital input status | INT16u | AB | 0 |  | X | X
Power meter area 1 | 46131 |  | 346132 | 04 |  | Is the communication to the mains power meter is alive. 0 = not alive, 1 = alive | INT16s | AB | 0 |  | X | X
PV monitoring area | 47000 |  | 347001 | 04 |  | Inverter serial number 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47001 |  | 347002 | 04 |  | Inverter serial number 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47002 |  | 347003 | 04 |  | Inverter serial number 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47003 |  | 347004 | 04 |  | Inverter serial number 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47004 |  | 347005 | 04 |  | Inverter serial number 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47005 |  | 347006 | 04 |  | Inverter serial number 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47006 |  | 347007 | 04 |  | Inverter serial number 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47007 |  | 347008 | 04 |  | Inverter serial number 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47008 |  | 347009 | 04 |  | Inverter serial number 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47009 |  | 347010 | 04 |  | Inverter serial number 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47010 |  | 347011 | 04 |  | Inverter serial number 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47011 |  | 347012 | 04 |  | Inverter serial number 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47012 |  | 347013 | 04 |  | Inverter serial number 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47013 |  | 347014 | 04 |  | Inverter serial number 27-28 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47014 |  | 347015 | 04 |  | Inverter serial number 19-30 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47015 |  | 347016 | 04 |  | Inverter serial number 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47016 |  | 347017 | 04 |  | Inverter model 01-02 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47017 |  | 347018 | 04 |  | Inverter model 03-04 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47018 |  | 347019 | 04 |  | Inverter model 05-06 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47019 |  | 347020 | 04 |  | Inverter model 07-08 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47020 |  | 347021 | 04 |  | Inverter model 09-10 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47021 |  | 347022 | 04 |  | Inverter model 11-12 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47022 |  | 347023 | 04 |  | Inverter model 13-14 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47023 |  | 347024 | 04 |  | Inverter model 15-16 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47024 |  | 347025 | 04 |  | Inverter model 17-18 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47025 |  | 347026 | 04 |  | Inverter model 19-20 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47026 |  | 347027 | 04 |  | Inverter model 21-22 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47027 |  | 347028 | 04 |  | Inverter model 23-24 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47028 |  | 347029 | 04 |  | Inverter model 25-26 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47029 |  | 347030 | 04 |  | Inverter model 27-28 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47030 |  | 347031 | 04 |  | Inverter model 19-30 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47031 |  | 347032 | 04 |  | Inverter model 31-32 (format maker-dependent) | string | AB | 0 |  | X | X
PV monitoring area | 47032 |  | 347033 | 04 |  | Rated active power size | INT16u | AB | 1 | kW | X | X
PV monitoring area | 47033 |  | 347034 | 04 |  | Rated reactive power size | INT16u | AB | 1 | kVAr | X | X
PV monitoring area | 47034 |  | 347035 | 04 |  | Country code (format maker-dependent) | INT16u | AB | 0 |  | X | X
PV monitoring area | 47035 |  | 347036 | 04 |  | DC voltage string 01 | INT16u | AB | 1 | V | X | X
PV monitoring area | 47036 |  | 347037 | 04 |  | DC power string 01 | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47037 |  | 347038 | 04 |  | DC voltage string 02 | INT16u | AB | 1 | V | X | X
PV monitoring area | 47038 |  | 347039 | 04 |  | DC power string 02 | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47039 |  | 347040 | 04 |  | DC voltage string 03 | INT16u | AB | 1 | V | X | X
PV monitoring area | 47040 |  | 347041 | 04 |  | DC power string 03 | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47041 |  | 347042 | 04 |  | DC voltage string 04 | INT16u | AB | 1 | V | X | X
PV monitoring area | 47042 |  | 347043 | 04 |  | DC power string 04 | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47043 |  | 347044 | 04 |  | AC active power | INT16s | AB | 1 | kW | X | X
PV monitoring area | 47044 |  | 347045 | 04 |  | AC reactive power | INT16s | AB | 1 | kVAr | X | X
PV monitoring area | 47045 |  | 347046 | 04 |  | AC apparent power | INT16s | AB | 1 | kVA | X | X
PV monitoring area | 47046 |  | 347047 | 04 |  | Energy produced | INT32u | ABCD | 0 | kWh | X | X
PV monitoring area | 47048 |  | 347049 | 04 |  | Energy produced today | INT32u | ABCD | 1 | kWh | X | X
PV monitoring area | 47050 |  | 347051 | 04 |  | Operating hours | INT32u | ABCD | 0 | hour | X | X
PV monitoring area | 47052 |  | 347053 | 04 |  | Operating minutes today | INT16u | AB | 0 | minute | X | X
PV monitoring area | 47053 |  | 347054 | 04 |  | Cabinet temperature | INT16s | AB | 1 | Deg C | X | X
PV monitoring area | 47054 |  | 347055 | 04 |  | Phase1 to neutral PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47055 |  | 347056 | 04 |  | Phase2 to neutral PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47056 |  | 347057 | 04 |  | Phase3 to neutral PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47057 |  | 347058 | 04 |  | Phase1 to phase2 PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47058 |  | 347059 | 04 |  | Phase2 to phase3 PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47059 |  | 347060 | 04 |  | Phase3 to phase1 PV voltage | INT16u | AB | 1 | V | X | X
PV monitoring area | 47060 |  | 347061 | 04 |  | Grid frequency | INT16u | AB | 1 | Hz | X | X
PV monitoring area | 47061 |  | 347062 | 04 |  | Active power reference (format maker-dependent) | INT16s | AB | 0 |  | X | X
PV monitoring area | 47062 |  | 347063 | 04 |  | Reactive power reference (format maker-dependent) | INT16s | AB | 0 |  | X | X
PV monitoring area | 47063 |  | 347064 | 04 |  | Inverter state (format maker-dependent) | INT16u | AB | 0 |  | X | X
PV monitoring area | 47064 |  | 347065 | 04 |  | Fault code (format maker-dependent) | INT16u | AB | 0 |  | X | X
PV monitoring area | 47069 |  | 347070 | 04 |  | 0: Inverter not alive on communication link. 1: Inverter alive on communication link. | INT16s | AB | 0 |  | X | X
PV monitoring area | 49940 |  | 349941 | 04 |  | PV monitoring version | INT16u | AB | 0 |  | X | X
PV monitoring area | 49941 |  | 349942 | 04 |  | PV protocol selection | INT16u | AB | 0 |  | X | X
PV monitoring area | 49942 |  | 349943 | 04 |  | PV protocol selection 01-02 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49943 |  | 349944 | 04 |  | PV protocol selection 03-04 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49944 |  | 349945 | 04 |  | PV protocol selection 05-06 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49945 |  | 349946 | 04 |  | PV protocol selection 07-08 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49946 |  | 349947 | 04 |  | PV protocol selection 09-10 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49947 |  | 349948 | 04 |  | PV protocol selection 11-12 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49948 |  | 349949 | 04 |  | PV protocol selection 13-14 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49949 |  | 349950 | 04 |  | PV protocol selection 15-16 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49950 |  | 349951 | 04 |  | PV protocol selection 17-18 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49951 |  | 349952 | 04 |  | PV protocol selection 19-20 (string access) | string | AB | 0 |  | X | X
PV monitoring area | 49952 |  | 349953 | 04 |  | Monitoring enabled: 0: Disabled. 1: Enabled | INT16u | AB | 0 |  | X | X
PV monitoring area | 49953 |  | 349954 | 04 |  | Number of inverter to monitor | INT16u | AB | 0 |  | X | X
PV monitoring area | 49954 |  | 349955 | 04 |  | Number of inverters missing | INT16u | AB | 0 |  | X | X
PV monitoring area | 49955 |  | 349956 | 04 |  | Lowest inverter ID missing | INT16u | AB | 0 |  | X | X
PV monitoring area | 49956 |  | 349957 | 04 |  | Highest inverter ID missing | INT16u | AB | 0 |  | X | X
PV monitoring area | 49957 |  | 349958 | 04 |  | P ref type: 0: Percentage. 1: kW | INT16u | AB | 0 |  | X | X
PV monitoring area | 49958 |  | 349959 | 04 |  | Q ref type: 0: Percentage. 1: kW. 2: Cos phi. 3: PF | INT16u | AB | 0 |  | X | X
PV monitoring area | 49959 |  | 349960 | 04 |  | P ref resolution: 0: zero decimals. 1: one decimal. 2: two decimals. 3: three decimals. | INT16u | AB | 0 |  | X | X
PV monitoring area | 49960 |  | 349961 | 04 |  | Q ref resolution: 0: zero decimals. 1: one decimal. 2: two decimals. 3: three decimals. | INT16u | AB | 0 |  | X | X
PV monitoring area | 49961 |  | 349962 | 04 |  | Lowest Modbus ID of the inverters | INT16u | AB | 0 |  | X | X