## About
iE 250 ML 300 Modbus texts | 4189341365 | Revision A
Software version
The information contained in this document is applicable to software version: |  |  | 1.0.23.x or later of the ML 300 products.
2.0.0.x or later of the iE 250 products.
How to use the look-up values
This example is where a controller has a status text on the display for Switchboard control.
Modbus address look up: | FC04 - 13900 | Texts - Controller status text
Gives value: | 90140008
Search in this table for: | 90140008
Gives the text: | Switchboard control

## Texts
Number | Title | Comment
0 | Undefined | Texts regarding engineering units / Label text
2 | A | Texts regarding engineering units / Label text
3 | kA | Texts regarding engineering units / Label text
4 | mA | Texts regarding engineering units / Label text
5 | V AC | Texts regarding engineering units / Label text
6 | kV AC | Texts regarding engineering units / Label text
7 | mV AC | Texts regarding engineering units / Label text
8 | W | Texts regarding engineering units / Label text
9 | kW | Texts regarding engineering units / Label text
10 | MW | Texts regarding engineering units / Label text
11 | Wh | Texts regarding engineering units / Label text
12 | kWh | Texts regarding engineering units / Label text
13 | MWh | Texts regarding engineering units / Label text
14 | VA | Texts regarding engineering units / Label text
15 | kVA | Texts regarding engineering units / Label text
16 | MVA | Texts regarding engineering units / Label text
17 | var | Texts regarding engineering units / Label text
18 | kvar | Texts regarding engineering units / Label text
19 | Mvar | Texts regarding engineering units / Label text
20 | varh | Texts regarding engineering units / Label text
21 | kvarh | Texts regarding engineering units / Label text
22 | Mvarh | Texts regarding engineering units / Label text
23 | s | Texts regarding engineering units / Label text
24 | ms | Texts regarding engineering units / Label text
25 | min | Texts regarding engineering units / Label text
26 | h | Texts regarding engineering units / Label text
27 | d | Texts regarding engineering units / Label text
28 | y | Texts regarding engineering units / Label text
29 | L | Texts regarding engineering units / Label text
30 | L/s | Texts regarding engineering units / Label text
31 | L/h | Texts regarding engineering units / Label text
32 | m | Texts regarding engineering units / Label text
33 | mm | Texts regarding engineering units / Label text
34 | km | Texts regarding engineering units / Label text
35 | °C | Texts regarding engineering units / Label text
36 | Hz | Texts regarding engineering units / Label text
37 | Hz/s | Texts regarding engineering units / Label text
38 | RPM | Texts regarding engineering units / Label text
39 | RPM/s | Texts regarding engineering units / Label text
40 | bar | Texts regarding engineering units / Label text
41 | bar/s | Texts regarding engineering units / Label text
42 | ohm | Texts regarding engineering units / Label text
43 | % | Texts regarding engineering units / Label text
44 | %/s | Texts regarding engineering units / Label text
45 | ° | Texts regarding engineering units / Label text
46 | periods | Texts regarding engineering units / Label text
48 | V DC | Texts regarding engineering units / Label text
49 | kV DC | Texts regarding engineering units / Label text
50 | mV DC | Texts regarding engineering units / Label text
52 | kPa | Texts regarding engineering units / Label text
54 | MPa | Texts regarding engineering units / Label text
55 | ppm | Texts regarding engineering units / Label text
56 | g/h | Texts regarding engineering units / Label text
57 | kg | Texts regarding engineering units / Label text
58 | g/kg | Texts regarding engineering units / Label text
59 | s/% | Texts regarding engineering units / Label text
1000 | Undefined | Texts regarding engineering units / Label text
1001 | No unit | Texts regarding engineering units / Label text
1002 | Current | Texts regarding engineering units / Label text
1003 | Current | Texts regarding engineering units / Label text
1004 | Current | Texts regarding engineering units / Label text
1005 | Voltage | Texts regarding engineering units / Label text
1006 | Voltage | Texts regarding engineering units / Label text
1007 | Voltage | Texts regarding engineering units / Label text
1008 | Active power | Texts regarding engineering units / Label text
1009 | Active power | Texts regarding engineering units / Label text
1010 | Active power | Texts regarding engineering units / Label text
1011 | Active power | Texts regarding engineering units / Label text
1012 | Kilowatt hour | Texts regarding engineering units / Label text
1013 | Megawatt hour | Texts regarding engineering units / Label text
1014 | Apparent power | Texts regarding engineering units / Label text
1015 | Apparent power | Texts regarding engineering units / Label text
1016 | Apparent power | Texts regarding engineering units / Label text
1017 | Reactive power | Texts regarding engineering units / Label text
1018 | Reactive power | Texts regarding engineering units / Label text
1019 | Reactive power | Texts regarding engineering units / Label text
1020 | Reactive power | Texts regarding engineering units / Label text
1021 | Reactive power | Texts regarding engineering units / Label text
1022 | Reactive power | Texts regarding engineering units / Label text
1023 | seconds | Texts regarding engineering units / Label text
1024 | milliseconds | Texts regarding engineering units / Label text
1025 | minutes | Texts regarding engineering units / Label text
1026 | hours | Texts regarding engineering units / Label text
1027 | days | Texts regarding engineering units / Label text
1028 | years | Texts regarding engineering units / Label text
1029 | litre | Texts regarding engineering units / Label text
1030 | litre | Texts regarding engineering units / Label text
1031 | litre | Texts regarding engineering units / Label text
1032 | meter | Texts regarding engineering units / Label text
1033 | millimeter | Texts regarding engineering units / Label text
1034 | kilometer | Texts regarding engineering units / Label text
1035 | Temperature | Texts regarding engineering units / Label text
1036 | Frequency | Texts regarding engineering units / Label text
1037 | Frequency | Texts regarding engineering units / Label text
1038 | Rotational speed | Texts regarding engineering units / Label text
1039 | Rotational speed | Texts regarding engineering units / Label text
1040 | Pressure | Texts regarding engineering units / Label text
1041 | Pressure | Texts regarding engineering units / Label text
1042 | Resistance | Texts regarding engineering units / Label text
1043 | percent | Texts regarding engineering units / Label text
1044 | percent | Texts regarding engineering units / Label text
1045 | degrees | Texts regarding engineering units / Label text
1046 | periods | Texts regarding engineering units / Label text
1047 | Power factor | Texts regarding engineering units / Label text
1048 | Voltage | Texts regarding engineering units / Label text
1049 | Voltage | Texts regarding engineering units / Label text
1050 | Voltage | Texts regarding engineering units / Label text
1051 | cos phi | Texts regarding engineering units / Label text
1052 | Pressure | Texts regarding engineering units / Label text
1054 | Pressure | Texts regarding engineering units / Label text
1055 | Mass | Texts regarding engineering units / Label text
1056 | Mass flow rate | Texts regarding engineering units / Label text
1057 | Mass | Texts regarding engineering units / Label text
1058 | Mass | Texts regarding engineering units / Label text
1059 | seconds | Texts regarding engineering units / Label text
7000 | Start/stop | Modbus address names / Menu text (menu hierachy and labels)
7001 | Generator breaker | Modbus address names / Menu text (menu hierachy and labels)
7002 | Alarms | Modbus address names / Menu text (menu hierachy and labels)
7003 | Modes | Modbus address names / Menu text (menu hierachy and labels)
7004 | Regulator | Modbus address names / Menu text (menu hierachy and labels)
7005 | Bus tie breaker | Modbus address names / Menu text (menu hierachy and labels)
7006 | Power management | Modbus address names / Menu text (menu hierachy and labels)
7007 | Shaft generator breaker | Modbus address names / Menu text (menu hierachy and labels)
7008 | Tie breaker | Modbus address names / Menu text (menu hierachy and labels)
7009 | Shore connection breaker | Modbus address names / Menu text (menu hierachy and labels)
7010 | Mains breaker | Modbus address names / Menu text (menu hierachy and labels)
7011 | Lamp test | Modbus address names / Menu text (menu hierachy and labels)
7012 | Quick-connect | Modbus address names / Menu text (menu hierachy and labels)
7013 | Priority | Modbus address names / Menu text (menu hierachy and labels)
7014 | Fieldbus | Modbus address names / Menu text (menu hierachy and labels)
7015 | Breaker | Modbus address names / Menu text (menu hierachy and labels)
7016 | ECU measurement auto discover | Modbus address names / Menu text (menu hierachy and labels)
7017 | J1939 Historical diagnostic log | Modbus address names / Menu text (menu hierachy and labels)
8000 | Start engine | Modbus address names / Modbus table text
8001 | Stop engine | Modbus address names / Modbus table text
8002 | Test engine | Modbus address names / Modbus table text
8003 | Engine start block | Modbus address names / Modbus table text
8004 | Reset engine start block | Modbus address names / Modbus table text
8005 | Start engine and close generator breaker | Modbus address names / Modbus table text
8006 | Open generator breaker and stop engine | Modbus address names / Modbus table text
8020 | Stay on DG supply after BTB close | Modbus address names / Modbus table text
8021 | Stay on SG/SC supply after BTB close | Modbus address names / Modbus table text
8037 | PTO request | Modbus address names / Modbus table text
8038 | PTI request | Modbus address names / Modbus table text
8039 | Standby request (Hybrid) | Modbus address names / Modbus table text
8100 | Breaker close | Modbus address names / Modbus table text
8101 | Breaker open | Modbus address names / Modbus table text
8300 | Activate static synchronisation | Modbus address names / Modbus table text
8301 | Deactivate static synchronisation | Modbus address names / Modbus table text
8302 | Activate dynamic synchronisation | Modbus address names / Modbus table text
8303 | Deactivate dynamic synchronisation | Modbus address names / Modbus table text
8310 | Activate static synchronisation | Modbus address names / Modbus table text
8311 | Deactivate static synchronisation | Modbus address names / Modbus table text
8312 | Activate dynamic synchronisation | Modbus address names / Modbus table text
8313 | Deactivate dynamic synchronisation | Modbus address names / Modbus table text
8400 | Activate MB static synchronisation | Modbus address names / Modbus table text
8401 | Deactivate MB static synchronisation | Modbus address names / Modbus table text
8402 | Activate MB dynamic synchronisation | Modbus address names / Modbus table text
8403 | Deactivate MB dynamic synchronisation | Modbus address names / Modbus table text
8410 | Activate TB static synchronisation | Modbus address names / Modbus table text
8411 | Deactivate TB static synchronisation | Modbus address names / Modbus table text
8412 | Activate TB dynamic synchronisation | Modbus address names / Modbus table text
8413 | Deactivate TB dynamic synchronisation | Modbus address names / Modbus table text
8500 | Quick-connect | Modbus address names / Modbus table text
8501 | Join | Modbus address names / Modbus table text
8502 | Leave | Modbus address names / Modbus table text
8503 | Reset | Modbus address names / Modbus table text
8504 | Cancel | Modbus address names / Modbus table text
8600 | Acknowledge all alarms | Modbus address names / Modbus table text
8601 | Acknowledge all alarms in system | Modbus address names / Modbus table text
8602 | Reset all latches | Modbus address names / Modbus table text
8603 | Reset alarm horn | Modbus address names / Modbus table text
8620 | Start lamp test | Modbus address names / Modbus table text
8621 | Stop lamp test | Modbus address names / Modbus table text
8640 | Group alarm | Modbus address names / Modbus table text
8650 | Fieldbus configuration command OK | Modbus address names / Modbus table text
8651 | Fieldbus configuration command Save | Modbus address names / Modbus table text
8652 | Fieldbus configuration command Cancel | Modbus address names / Modbus table text
8653 | Fieldbus conflict accepted | Modbus address names / Modbus table text
8660 | Accept firmware module update | Modbus address names / Modbus table text
8661 | Postpone firmware module update | Modbus address names / Modbus table text
8670 | Measurement list filter - available | Modbus address names / Modbus table text
8671 | Measurement list filter - clear | Modbus address names / Modbus table text
8680 | Log request (DM2) | Modbus address names / Modbus table text
8681 | Log clear (DM2) | Modbus address names / Modbus table text
8700 | AUTO | Modbus address names / Modbus table text
8701 | MANUAL | Modbus address names / Modbus table text
8702 | Force all gensets in section to AUTO | Modbus address names / Modbus table text
8703 | Force all gensets in section to MANUAL | Modbus address names / Modbus table text
8706 | Local command control | Modbus address names / Modbus table text
8707 | Remote command control | Modbus address names / Modbus table text
8708 | NO REG | Modbus address names / Modbus table text
8709 | TEST | Modbus address names / Modbus table text
8800 | GOV increase ON | Modbus address names / Modbus table text
8801 | GOV increase OFF | Modbus address names / Modbus table text
8802 | GOV decrease ON | Modbus address names / Modbus table text
8803 | GOV decrease OFF | Modbus address names / Modbus table text
8804 | AVR increase ON | Modbus address names / Modbus table text
8805 | AVR increase OFF | Modbus address names / Modbus table text
8806 | AVR decrease ON | Modbus address names / Modbus table text
8807 | AVR decrease OFF | Modbus address names / Modbus table text
8808 | Reset manual GOV/AVR | Modbus address names / Modbus table text
8810 | GOV activate fixed frequency | Modbus address names / Modbus table text
8811 | GOV deactivate fixed frequency | Modbus address names / Modbus table text
8812 | GOV activate fixed power | Modbus address names / Modbus table text
8813 | GOV deactivate fixed power | Modbus address names / Modbus table text
8814 | GOV activate frequency droop | Modbus address names / Modbus table text
8815 | GOV deactivate frequency droop | Modbus address names / Modbus table text
8816 | GOV activate load sharing | Modbus address names / Modbus table text
8817 | GOV deactivate load sharing | Modbus address names / Modbus table text
8818 | GOV activate external set point (network) | Modbus address names / Modbus table text
8819 | GOV deactivate external set point (network) | Modbus address names / Modbus table text
8820 | GOV activate external set point | Modbus address names / Modbus table text
8821 | GOV deactivate external set point | Modbus address names / Modbus table text
8822 | GOV activate external set point | Modbus address names / Modbus table text
8823 | GOV deactivate external set point | Modbus address names / Modbus table text
8824 | GOV activate manual | Modbus address names / Modbus table text
8825 | GOV deactivate manual | Modbus address names / Modbus table text
8850 | AVR activate fixed voltage | Modbus address names / Modbus table text
8851 | AVR deactivate fixed voltage | Modbus address names / Modbus table text
8852 | AVR activate fixed reactive power | Modbus address names / Modbus table text
8853 | AVR deactivate fixed reactive power | Modbus address names / Modbus table text
8854 | AVR activate fixed cos phi | Modbus address names / Modbus table text
8855 | AVR deactivate fixed cos phi | Modbus address names / Modbus table text
8856 | AVR activate reactive power load sharing | Modbus address names / Modbus table text
8857 | AVR deactivate reactive power load sharing | Modbus address names / Modbus table text
8858 | AVR activate voltage droop | Modbus address names / Modbus table text
8859 | AVR deactivate voltage droop | Modbus address names / Modbus table text
8860 | AVR activate external set point (network) | Modbus address names / Modbus table text
8861 | AVR deactivate external set point (network) | Modbus address names / Modbus table text
8862 | AVR activate external set point | Modbus address names / Modbus table text
8863 | AVR deactivate external set point | Modbus address names / Modbus table text
8864 | AVR activate external set point | Modbus address names / Modbus table text
8865 | AVR deactivate external set point | Modbus address names / Modbus table text
8866 | AVR activate manual | Modbus address names / Modbus table text
8867 | AVR deactivate manual | Modbus address names / Modbus table text
8868 | Regulator on | Modbus address names / Modbus table text
8869 | Regulator off | Modbus address names / Modbus table text
8900 | First priority | Modbus address names / Modbus table text
8901 | Precautionary genset start | Modbus address names / Modbus table text
8902 | Reset precautionary genset start | Modbus address names / Modbus table text
8903 | Harbour mode on request | Modbus address names / Modbus table text
8904 | Harbour mode off request | Modbus address names / Modbus table text
8905 | Allow harbour operation | Modbus address names / Modbus table text
8906 | Last priority | Modbus address names / Modbus table text
8907 | Priority trigger | Modbus address names / Modbus table text
8908 | Global auto start | Modbus address names / Modbus table text
8909 | Global auto stop | Modbus address names / Modbus table text
8910 | Secured mode on | Modbus address names / Modbus table text
8911 | Secured mode off | Modbus address names / Modbus table text
9000 | Generator breaker close | Modbus address names / Modbus table text
9001 | Generator breaker open | Modbus address names / Modbus table text
9002 | Generator breaker close block | Modbus address names / Modbus table text
9003 | Reset generator breaker close block | Modbus address names / Modbus table text
9004 | Activate breaker close | Modbus address names / Modbus table text
9005 | Deactivate breaker close | Modbus address names / Modbus table text
9006 | Generator breaker open without de-loading | Modbus address names / Modbus table text
9010 | Tie breaker close | Modbus address names / Modbus table text
9011 | Tie breaker open | Modbus address names / Modbus table text
9012 | Tie breaker close block | Modbus address names / Modbus table text
9013 | Reset tie breaker close block | Modbus address names / Modbus table text
9014 | Tie breaker open without de-loading | Modbus address names / Modbus table text
9020 | Bus tie breaker close | Modbus address names / Modbus table text
9021 | Bus tie breaker open | Modbus address names / Modbus table text
9022 | Bus tie breaker close block | Modbus address names / Modbus table text
9023 | Reset bus tie breaker close block | Modbus address names / Modbus table text
9024 | Bus tie breaker open without de-loading | Modbus address names / Modbus table text
9030 | Shaft generator breaker close | Modbus address names / Modbus table text
9031 | Shaft generator breaker open | Modbus address names / Modbus table text
9032 | Shaft generator breaker close block | Modbus address names / Modbus table text
9033 | Reset shaft generator breaker close block | Modbus address names / Modbus table text
9034 | Shaft generator breaker open without de-loading | Modbus address names / Modbus table text
9040 | Shore connection breaker close | Modbus address names / Modbus table text
9041 | Shore connection breaker open | Modbus address names / Modbus table text
9042 | Shore connection breaker close block | Modbus address names / Modbus table text
9043 | Reset shore connection breaker close block | Modbus address names / Modbus table text
9044 | Shore connection breaker open without de-loading | Modbus address names / Modbus table text
9045 | Shore connection breaker action open | Modbus address names / Modbus table text
9046 | Shore connection breaker action open without de-loading | Modbus address names / Modbus table text
9047 | Shore connection breaker action cancel | Modbus address names / Modbus table text
9050 | Mains breaker close | Modbus address names / Modbus table text
9051 | Mains breaker open | Modbus address names / Modbus table text
9052 | Mains breaker close block | Modbus address names / Modbus table text
9053 | Reset mains breaker close block | Modbus address names / Modbus table text
9054 | Mains breaker open without de-loading | Modbus address names / Modbus table text
9062 | Block breaker close | Modbus address names / Modbus table text
9063 | Reset breaker close block | Modbus address names / Modbus table text
9064 | Block breaker open | Modbus address names / Modbus table text
9065 | Reset breaker open block | Modbus address names / Modbus table text
9066 | Breaker open without de-loading | Modbus address names / Modbus table text
9070 | Start | Modbus address names / Modbus table text
9071 | Stop | Modbus address names / Modbus table text
9500 | Join | Modbus address names / Modbus table text
9501 | Leave | Modbus address names / Modbus table text
9502 | Cancel | Modbus address names / Modbus table text
9503 | Reset | Modbus address names / Modbus table text
1000000 | AC configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000001 | Engine | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000002 | Generator | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000003 | Busbar | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000004 | Busbar A | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000005 | Busbar B | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000006 | Shore busbar | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000007 | Ship busbar | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000008 | Regulators | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000009 | Breakers | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000010 | Local power management | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000011 | Configuration 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000012 | Configuration 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000013 | Configuration 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000014 | Configuration 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000015 | Configuration 5 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000016 | Configuration 6 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000017 | Configuration 7 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000018 | Configuration 8 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000019 | System power management | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000020 | Power supply | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000021 | 4th current input | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000022 | Alarm horn | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000023 | Utility | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000024 | Load sharing | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000025 | Non-essential load trip | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000026 | Custom alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000027 | Synchronisation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000028 | System alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000029 | Mains | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000031 | Hardware | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000032 | Monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000033 | Additional functions | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000034 | Single-line | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000035 | Alarm system | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000036 | Test functions | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000037 | Local | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000038 | Modbus | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000039 | DEIF network | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000040 | Auxiliary | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000041 | NTP | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000042 | Power management rules | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000043 | Alive | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000044 | Load reduction | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000050 | Transducers | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000060 | Fieldbus | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000061 | Custom parameters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000062 | Inverter | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000063 | CAN bus | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000064 | CPU | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000065 | Custom alarm | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000066 | Custom counters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000067 | Power transformer | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1000068 | Fan | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050000 | System | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050001 | Step-up transformer | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050002 | Additional protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050050 | Start sequence | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050051 | Stop sequence | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050052 | Running detection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050053 | RPM | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050054 | Protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050055 | Derate 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050056 | Derate 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050057 | Derate 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050058 | Maintenance | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050059 | Fuel control | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050060 | Power derate | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050061 | Emergency stop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050062 | RPM power derate 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050063 | Analogue input power derate 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050064 | Temperature | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050065 | Percentage | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050066 | Measurements | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050067 | Speed | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050068 | Level | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050069 | Pressure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050070 | Safety shutdown | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050071 | Keep stop coil active | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050072 | Idle run start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050073 | Idle run stop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050100 | Nominal settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050101 | Fixed power setting | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050102 | Fixed cos phi setting | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050103 | Current protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050104 | Voltage protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050105 | Frequency protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050106 | Power protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050107 | Reactive power protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050108 | AC settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050109 | Energy counters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050110 | Frequency-dependent power droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050111 | Voltage-dependent reactive power droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050112 | Voltage-dependent cos phi droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050113 | AC setup | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050114 | Power-dependent reactive power droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050115 | Power-dependent cos phi droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050116 | RPM derated power protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050117 | Production counters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050118 | Base load | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050125 | Trip 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050126 | Trip 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050127 | Trip 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050128 | Reduction output 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050129 | Reduction output 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050150 | Voltage protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050151 | Frequency protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050152 | Current protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050153 | Power protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050154 | Reactive power protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050200 | GOV | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050201 | GOV analogue configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050202 | GOV relay configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050203 | GOV general configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050204 | AVR | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050205 | AVR analogue configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050206 | AVR relay configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050207 | AVR general configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050208 | GOV monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050209 | AVR monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050210 | GOV regulation set points | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050211 | AVR regulation set points | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050212 | Common | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050221 | Alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050222 | Advanced blackout prevention | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050250 | Generator breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050251 | Tie breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050252 | Bus tie breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050253 | Shore connection breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050254 | Shaft generator breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050259 | Mains breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050260 | Generator breaker configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050261 | Generator breaker monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050262 | Tie breaker configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050263 | Tie breaker monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050264 | Bus tie breaker configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050265 | Bus tie breaker monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050266 | Mains breaker configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050267 | Mains breaker monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050272 | Shaft breaker configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050273 | Shaft breaker monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050274 | Shore breaker configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050275 | Shore breaker monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050276 | %s feedback monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050277 | Inverter breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050278 | Inverter breaker configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050279 | Inverter breaker monitoring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050300 | Alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050301 | Communication | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050302 | Return modes | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050303 | Asymmetric load sharing | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050304 | Load-dependent start/stop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050305 | Priority | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050306 | Power reservation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050307 | Emergency generator | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050308 | Shaft generator base load | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050309 | Shore connection base load | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050310 | Shore connection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050311 | Blackout | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050312 | Parallel timers | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050313 | Number of gensets connected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050314 | Non-connected genset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050315 | Network | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050316 | Shaft generator PTH mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050317 | Bus tie breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050318 | Shore connection ship-to-ship | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050319 | Shore connection close load | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050320 | Shaft generator f [Hz] variation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050321 | Load-dependent start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050322 | Load-dependent stop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050323 | Automatic start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050324 | Delays | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050325 | Hybrid modes | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050326 | Plant/genset mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050327 | Command mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050328 | Mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050329 | Update | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050330 | Set point offsets | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050331 | Store common settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050550 | Remote | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050551 | System OK | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050600 | Horn 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050601 | Horn 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050602 | Horn 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050700 | Digital | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050701 | Analogue | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050800 | CustomLogic | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050801 | Alarm test | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050802 | Lamp test | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050803 | Action | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050804 | Command sources | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050805 | AC measurement filters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050806 | Primary AC measurements | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1050900 | Emulation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051000 | Settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051001 | Alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051002 | Synchronisation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051100 | Alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051101 | Project | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051200 | Fuel pump | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051300 | ECU | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051301 | Digital AVR | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051302 | Fan clutch | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051303 | Battery charger | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051304 | Diagnostic | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051420 | Transducer %s | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051500 | Custom parameter %s | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1051800 | Custom alarm %s | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1052000 | Custom counters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100000 | Phase configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100001 | Phase direction | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100002 | Multiple phase wire break | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100003 | L1 wire break | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100004 | L2 wire break | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100005 | L3 wire break | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100100 | Phase sequence error | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100101 | Voltage and frequency OK | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100102 | Voltage and frequency OK (blackout) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100103 | Voltage or frequency not OK | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100104 | Voltage transformer | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100105 | Current transformer | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100106 | Current transformer (I4) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100107 | Blackout detection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100108 | Power measurement | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100109 | Supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100110 | Generator type | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100111 | No synchronisation signal | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100112 | Asynchronous over-voltage | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100113 | Supervision alarm | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100114 | Supervision selector | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100115 | CT - ACM3.2 - Consumer side | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100116 | CT - ACM3.2 - Neutral side | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100117 | Current transformer (ACM3.2) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100118 | Mains power measurement | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100150 | Reference A | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100151 | Reference B | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100200 | Transformer type | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100201 | Controller nominal setting | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1100219 | Transducer %s nominal setting | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101000 | Idle run | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101001 | Start prepare | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101002 | Run coil | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101003 | Stop coil | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101004 | Crank | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101005 | Start attempts | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101006 | Start failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101007 | Crank failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101008 | Externally started | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101009 | Start enable removed during start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101010 | Restrictions | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101011 | Start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101012 | Run detection not reached | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101100 | Cooldown | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101101 | Extended stop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101102 | Stop failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101103 | Externally stopped | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101200 | Feedback type | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101201 | Engine ready | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101202 | Frequency running detection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101203 | Primary running feedback failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101204 | RPM running detection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101205 | Oil pressure running detection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101300 | MPU setup | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101301 | Nominal RPM | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101400 | Overspeed 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101401 | Overspeed 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101402 | Under-speed 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101403 | Under-speed 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101404 | Magnetic pickup wire break | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101405 | Oil pressure 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101406 | Oil pressure 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101407 | Oil temperature 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101408 | Oil temperature 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101409 | Coolant temperature 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101410 | Coolant temperature 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101411 | Coolant temperature 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101412 | Coolant level 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101413 | Coolant level 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101414 | Coolant level 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101415 | Coolant temperature | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101416 | Oil temperature | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101417 | External condition | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101418 | Coolant | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101419 | Lube oil | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101420 | Speed | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101500 | Enable | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101501 | Setup | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101502 | Open point | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101503 | Connect load | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101600 | Priming | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101700 | Running hours total | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101701 | Operation time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101712 | Running hours trip %s | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101713 | Service timer | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101801 | Fuel pump logic | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101802 | Service timers | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101900 | Air ambient | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101901 | Air cooler | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101902 | Coolant | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101903 | Engine counters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101904 | DPF | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101905 | Engine load | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101906 | Exhaust gas | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101907 | Fuel | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101908 | Information | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101909 | Lube oil | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101910 | Pressure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101911 | Speed | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101912 | Temperature | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101913 | Turbo charger | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101914 | Intake | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101915 | Controls | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101916 | Diagnostic alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101917 | Manufacture specific | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1101918 | DPF controls | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102000 | Calculation method | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102001 | Nominal settings 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102002 | Nominal settings 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102003 | Nominal settings 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102004 | Nominal settings 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102005 | Voltage (V) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102006 | Current (I) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102007 | Frequency (f) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102008 | Current (I4) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102009 | Phase angle | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102010 | Frequency (f) (from voltage) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102011 | Frequency (f) (from current) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102012 | Current (I4) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102013 | Active energy export | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102014 | Reactive energy export | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102015 | Active energy import | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102016 | Reactive energy import | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102017 | Active energy difference | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102018 | Reactive energy difference | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102019 | Current (I) - ACM3.2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102020 | Nominal settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102021 | Frequency (f) - ACM3.2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102100 | Fixed P setting | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102200 | Fixed PF setting | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102300 | Over-current 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102301 | Over-current 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102302 | Fast over-current 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102303 | Fast over-current 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102304 | Current unbalance (average calc.) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102305 | Current unbalance (nominal calc.) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102306 | Directional over-current 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102307 | Directional over-current 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102308 | Inverse time over-current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102309 | Earth inverse time over-current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102310 | Neutral inverse time over-current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102311 | Voltage-dependent over-current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102312 | Negative sequence current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102313 | Zero sequence current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102314 | V< and Q< settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102315 | Directional over-current 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102316 | Directional over-current 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102317 | Stabilised differential current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102318 | High set differential current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102319 | Over-current 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102320 | Over-current 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102400 | Over-voltage 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102401 | Over-voltage 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102402 | Under-voltage 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102403 | Under-voltage 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102404 | Voltage unbalance | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102405 | Negative sequence voltage | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102406 | Zero sequence voltage | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102407 | Positive sequence under-voltage | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102408 | Over-voltage average 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102409 | Over-voltage average 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102410 | Over-voltage aggregation settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102411 | Under-voltage 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102412 | Under-voltage 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102413 | Over-voltage 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102500 | Over-frequency 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102501 | Over-frequency 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102502 | Under-frequency 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102503 | Under-frequency 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102504 | Under-frequency 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102505 | Under-frequency 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102506 | Over-frequency 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102600 | Overload 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102601 | Overload 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102602 | Reverse power 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102603 | Reverse power 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102604 | Power export 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102605 | Power export 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102606 | Power import 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102607 | Power import 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102608 | Overload reverse power 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102609 | Overload reverse power 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102610 | Overload 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102611 | Overload 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102612 | Overload 5 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102613 | Power export 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102614 | Power export 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102615 | Power export 5 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102616 | Power import 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102617 | Power import 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102618 | Power import 5 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102700 | Reactive power export 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102701 | Reactive power export 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102702 | Reactive power import 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102703 | Reactive power import 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102704 | Power-dependent over-excitation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102705 | Power-dependent under-excitation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102800 | Over-current | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102801 | Under-frequency | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102802 | Overload 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102803 | Overload 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102804 | Reactive overload | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102805 | Settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102900 | RPM derated power overload 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102901 | RPM derated power overload 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102950 | Low power available [kW] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1102951 | Low power available [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103000 | Active power offset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103001 | Frequency droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103002 | Frequency regulation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103003 | Frequency synchronisation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103004 | Phase synchronisation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103005 | Power regulation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103006 | Power load sharing regulation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103007 | RPM synchronisation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103008 | RPM regulation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103009 | Cos phi/reactive power offset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103010 | Automatic configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103011 | Manual configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103012 | Regulator mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103200 | Active power ramp up | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103201 | Active power ramp down | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103202 | Power ramp up error | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103203 | Power ramp down error | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103204 | Manual slope | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103205 | External offset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103206 | Regulation error | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103207 | Regulator output | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103208 | Regulation delay | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103209 | Regulation mode not selected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103210 | Multiple regulator modes selected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103211 | Fixed power | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103212 | Fixed reactive power | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103213 | Stand-alone configuration error | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103214 | Fixed cos phi | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103215 | Reactive power ramp up | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103216 | Reactive power ramp down | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103217 | Stand-alone configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103218 | Fixed cos phi offset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103219 | Fixed cos phi limit | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103220 | Active power ramp configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103221 | Active power ramps | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103222 | Fixed reactive power offset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103223 | Fixed reactive power limit | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103224 | Fixed power offset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103225 | Fixed power limit | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103226 | Cos phi | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103227 | Active power | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103228 | Active power operation ramp | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103229 | Active power enter operation ramp | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103230 | Active power deload ramp | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103231 | Reactive power operation ramp | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103300 | Voltage droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103301 | Voltage regulation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103302 | Reactive power regulation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103303 | Reactive power load sharing regulation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103400 | P load sharing failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103401 | Q load sharing failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103402 | Delay after load share changes | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103403 | P load sharing failure (low frequency) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103404 | P load sharing failure (high frequency) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103405 | Q load sharing failure (low voltage) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103406 | Q load sharing failure (high voltage) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103407 | Overload on a DG | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103408 | Reverse power on a DG | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103409 | Reactive power export on a DG | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103410 | Reactive power import on a DG | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103411 | Over-current on a DG | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103500 | Modes | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103501 | Manual | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103521 | External set points | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1103522 | Offset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104000 | Configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104001 | Opening failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104002 | Closing failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104003 | Position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104004 | Tripped (external) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104005 | Synchronisation failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104006 | De-load failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104007 | Short circuit | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104008 | Vector mismatch | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104009 | Synchronisation setting | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104010 | Synchronisation setting (PTH) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104011 | Controls | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104012 | State | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104013 | Command | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104014 | Feedback | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104015 | Function | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104016 | P configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104017 | Q configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104018 | Configuration failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104019 | Sync. status | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104020 | De-load last breaker | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104021 | Feedback mismatch | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104022 | Protective start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104023 | BTB 33 position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104024 | BTB 34 position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104025 | BTB 35 position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104026 | BTB 36 position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104027 | BTB 37 position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104028 | BTB 38 position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104029 | BTB 39 position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104030 | BTB 40 position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1104031 | Severity | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105003 | Forced to switchboard control | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105004 | Forced to MANUAL mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105005 | Busbar blocked | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105006 | Mains configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105007 | N+X | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105010 | Section | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105011 | Plant | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105100 | Stop timer | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105101 | Maximum | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105102 | Minimum | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105103 | PTH minimum | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105104 | SG-DG max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105105 | DG-SG max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105106 | DG-SC max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105107 | EDG max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105108 | SC-DG max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105109 | SG-SG max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105110 | SC-SG max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105111 | SC-SC max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105112 | Hybrid-SG max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105113 | Hybrid-SC max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105114 | SG-Hybrid max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105115 | SC-Hybrid max. parallel time | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105116 | Minimum set 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105117 | Minimum set 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105200 | Heavy consumer | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105201 | Start 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105202 | Start 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105203 | Stop 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105204 | Stop 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105205 | Start when an asymmetric set point is exceeded | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105210 | Startup | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105220 | Active power 1 [kW] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105221 | Active power 2 [kW] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105222 | Active power 3 [kW] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105225 | Active power 1 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105226 | Active power 2 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105227 | Active power 3 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105230 | Reactive power 1 [kvar] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105231 | Reactive power 2 [kvar] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105232 | Reactive power 3 [kvar] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105235 | Reactive power 1 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105236 | Reactive power 2 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105237 | Reactive power 3 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105240 | Apparent power 1 [kVA] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105241 | Apparent power 2 [kVA] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105242 | Apparent power 3 [kVA] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105245 | Apparent power 1 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105246 | Apparent power 2 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105247 | Apparent power 3 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105250 | Active power 1 [kW] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105251 | Active power 2 [kW] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105252 | Active power 3 [kW] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105255 | Active power 1 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105256 | Active power 2 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105257 | Active power 3 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105260 | Reactive power 1 [kvar] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105261 | Reactive power 2 [kvar] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105262 | Reactive power 3 [kvar] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105265 | Reactive power 1 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105266 | Reactive power 2 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105267 | Reactive power 3 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105270 | Apparent power 1 [kVA] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105271 | Apparent power 2 [kVA] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105272 | Apparent power 3 [kVA] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105275 | Apparent power 1 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105276 | Apparent power 2 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105277 | Apparent power 3 [%] | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105300 | Selection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105301 | Delayed priority shift | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105302 | Running hours | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105303 | Manual | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105304 | Priority list | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105400 | Secured mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105401 | Reserved power | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105402 | Mains power | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105403 | Peak shaving | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105404 | Mains test | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105405 | Genset test | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105406 | Time settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105500 | Test delay | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105501 | Test base load | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105502 | After EDG test | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105503 | Test type | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105504 | Blackout handling | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105505 | EDG not ready for blackout | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105506 | Operator confirms harbour operation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105507 | Solo supply harbour operation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105600 | Power set point | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105601 | Min. set point | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105602 | Max. set point | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105700 | Closed ring | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105701 | Parallel | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105702 | Supply mode after BTB close | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105703 | Short-circuit limitation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105704 | Commands | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105800 | Blackout close | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105801 | Short circuit close attempts | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105802 | Blackout recovery | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105803 | Blackout detection mismatch | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105900 | Reservation not possible | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105901 | Feedback timeout | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105902 | Acknowledge | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1105903 | Request signal | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106100 | After SWBD control | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106101 | After blackout | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106200 | DEIF network redundancy broken | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106201 | Modbus communication timeout | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106202 | DEIF network top ring redundancy broken | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106203 | P delay after connect | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106204 | CAN-A bus off | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106205 | CAN-B bus off | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106206 | DEIF network has only one connection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106207 | DEIF network fork detected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106208 | DEIF network top ring has only one connection | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106209 | DEIF network top ring fork detected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106300 | Frequency [Hz] variation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106301 | Engine start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106302 | Connect gensets | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106400 | NTP server 1 not connected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106401 | NTP server 1 no response | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106402 | NTP server 2 not connected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106403 | NTP server 2 no response | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106404 | No NTP server(s) connected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106405 | No NTP server time synchronisation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106500 | I/O configuration - Ext. rack | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106501 | I/O configuration - Module | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106502 | Fieldbus conflict | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106503 | Fieldbus connection missing | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106600 | Standby | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106601 | PTO (power take off) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1106602 | PTI (power take in) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107000 | Diode compensation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107001 | Low voltage alarm | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107002 | High voltage alarm | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107003 | Relay 4 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107004 | Status not OK alarm | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107005 | Load | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107006 | Relay 9 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107007 | Relay 10 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107008 | Relay 11 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107009 | Relay 12 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107010 | Relay 13 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107011 | Relay 14 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107012 | Relay 15 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107013 | Relay 16 supervision | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107014 | Core 1 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107015 | Core 2 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107016 | Core 3 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1107017 | Core 4 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1108000 | Frequency window | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1108001 | Voltage window | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1108002 | Type | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109000 | Missing all controllers | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109001 | Duplicate controller ID | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109002 | Missing any controller | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109003 | Any bus tie breaker position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109004 | Mode while controller missing | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109005 | PMS mode while controller missing | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109006 | Missing controllers | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109007 | Any mains breaker position failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109008 | NTP server not connected | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109009 | NTP server not responding | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109010 | Group alarm | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109011 | Data loss from a controller | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109012 | Data loss on DEIF network | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109013 | High traffic on DEIF network | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109014 | Missing controllers and groups | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1109015 | Single-line hazard | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1110000 | Not under remote control | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1110100 | System not OK | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1110200 | Fuel fill alarm | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1110201 | Fuel pump settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1110300 | Active sources | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1110301 | Active local sources | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1110302 | Active remote sources | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1110400 | Alive configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111000 | Application not OK | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111001 | I/O config conflict | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111002 | Outputs | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111003 | Values | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111004 | VTA | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111005 | Modbus | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111100 | Boolean values | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111101 | Integer values | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111102 | Float values | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111104 | Modbus coil | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111105 | Modbus input | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111106 | Modbus holding | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1111107 | Modbus register | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113000 | Voltage transformer | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113001 | Settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113002 | Droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113003 | Advanced settings | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113004 | Protections | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113005 | Controls | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113006 | Alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113007 | Parameters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113008 | Load acceptance module | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113009 | Soft voltage recovery | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113010 | Start on threshold | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113011 | Operation modes | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113012 | U/f variable slope | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113013 | Soft start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113014 | Current limitation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113015 | Magnetisation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113016 | Inductive motor starting | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113017 | PID | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113018 | Bias | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113019 | Reset soft start | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113020 | LED | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113021 | Pt100 | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113022 | PTC | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113023 | Wire break | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113024 | Supply | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1113025 | Illegal configuration | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1114000 | Active alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1114001 | Historical alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1115000 | Close before excitation | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1115001 | CBE failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1115002 | CBE rerun failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1116000 | Short-time parallel | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200000 | Power (P) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200001 | Reactive power (Q) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200002 | Apparent power (S) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200003 | Power factor (PF) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200100 | Request failure | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200101 | Acknowledge timeout | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200200 | Bus off | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200201 | ECU | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200202 | Digital AVR | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200500 | Speed control (TSC1 / Custom) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200501 | Generator control (GC1 / Custom) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200502 | Cab message (CM1 / Custom) | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200503 | Shutdown override | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200504 | Parameters | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200505 | CAN controls | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200506 | Alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200507 | Controls | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200508 | Controls | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200509 | Droop | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200510 | Speed demand switch position | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1200511 | Reset | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500000 | Inhibits | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500001 | Alarm | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500002 | Mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500003 | Power management | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500004 | CustomLogic | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500005 | Outputs | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500006 | Inputs | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500007 | Load sharing | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500008 | Heavy consumers | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500009 | Supply mode | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500010 | System alarms | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
1500011 | Quick-connect | Texts related to menu hierarchy on UI's / Menu text (menu hierachy and labels)
2000000 | Outputs | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2000001 | Inputs | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2000004 | ICC | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2000006 | Measurements | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2000007 | Modbus signals | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2000008 | Stored flags | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2000009 | Configuration invalid | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2050000 | Outputs | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2050001 | Inputs | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
2050002 | Any | Texts regarding CustomLogic / Menu text (menu hierachy and labels)
3200090 | Vector mismatch | Texts related to synchronisation / Parameter name
3200100 | Vector mismatch | Texts related to synchronisation / Parameter name
3210090 | Vector mismatch | Texts related to synchronisation / Parameter name
3210100 | Vector mismatch | Texts related to synchronisation / Parameter name
3220090 | Vector mismatch | Texts related to synchronisation / Parameter name
3220100 | Vector mismatch | Texts related to synchronisation / Parameter name
3230090 | Vector mismatch | Texts related to synchronisation / Parameter name
3230100 | Vector mismatch | Texts related to synchronisation / Parameter name
3240090 | Vector mismatch | Texts related to synchronisation / Parameter name
3240100 | Vector mismatch | Texts related to synchronisation / Parameter name
3300090 | Breaker vector mismatch | Texts related to synchronisation / Alarm text (pop-ups and logs)
3300100 | Breaker vector mismatch | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
3300110 | Delta speed min. | Texts related to synchronisation / Parameter name
3300120 | Delta speed max. | Texts related to synchronisation / Parameter name
3306001 | Breaker static synchronisation | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
3306002 | Breaker dynamic synchronisation | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
3310090 | Breaker vector mismatch | Texts related to synchronisation / Alarm text (pop-ups and logs)
3310100 | Breaker vector mismatch | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
3310110 | Delta speed min. | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
3310120 | Delta speed max. | Texts related to synchronisation / Parameter name
3316001 | Breaker static synchronisation | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
3316002 | Breaker dynamic synchronisation | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
4000000 | DG | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000001 | PMS info | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000002 | Alarm | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000003 | Menu | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000004 | Back | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000005 | Mode | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000006 | Run | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000007 | Gen Power S P Q | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000008 | Current L1-L2-L3 | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000009 | Gen Volt Freq. | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000010 | Generator | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000011 | Busbar | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000012 | Log | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000013 | AOP | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000014 | 1st | Texts related to AGI solutions. / Miscellaneous text (various uses)
4000015 | I/O | Texts related to AGI solutions. / Miscellaneous text (various uses)
5000000 | View 1 | Texts related to display. / Used in view designs
5000001 | View 2 | Texts related to display. / Used in view designs
5000002 | View 3 | Texts related to display. / Used in view designs
5000003 | View 4 | Texts related to display. / Used in view designs
5000004 | View 5 | Texts related to display. / Used in view designs
5000005 | View 6 | Texts related to display. / Used in view designs
5000006 | View 7 | Texts related to display. / Used in view designs
5000007 | View 8 | Texts related to display. / Used in view designs
5000008 | View 9 | Texts related to display. / Used in view designs
5000009 | View 10 | Texts related to display. / Used in view designs
5000010 | View 11 | Texts related to display. / Used in view designs
5000011 | View 12 | Texts related to display. / Used in view designs
5000012 | View 13 | Texts related to display. / Used in view designs
5000013 | View 14 | Texts related to display. / Used in view designs
5000014 | View 15 | Texts related to display. / Used in view designs
5000015 | View 16 | Texts related to display. / Used in view designs
5000016 | View 17 | Texts related to display. / Used in view designs
5000017 | View 18 | Texts related to display. / Used in view designs
5000018 | View 19 | Texts related to display. / Used in view designs
5000019 | View 20 | Texts related to display. / Used in view designs
5000020 | View 21 | Texts related to display. / Used in view designs
5000021 | View 22 | Texts related to display. / Used in view designs
5000022 | View 23 | Texts related to display. / Used in view designs
5000023 | View 24 | Texts related to display. / Used in view designs
5000024 | View 25 | Texts related to display. / Used in view designs
5000025 | View 26 | Texts related to display. / Used in view designs
5000026 | View 27 | Texts related to display. / Used in view designs
5000027 | View 28 | Texts related to display. / Used in view designs
5000028 | View 29 | Texts related to display. / Used in view designs
5000029 | View 30 | Texts related to display. / Used in view designs
10000000 | Application initialisation error | Texts regarding system behaviour / Alarm text (pop-ups and logs)
10000010 | Application configuration changed. The controller rack must be powered off and on for changes to take effect | Texts regarding system behaviour / Alarm text (pop-ups and logs)
10100000 | Application initialised correctly | Texts regarding system behaviour / Event text (pop-ups, logs and status texts)
10100010 | Application initialise failed | Texts regarding system behaviour / Event text (pop-ups, logs and status texts)
10100020 | Download of new software | Texts regarding system behaviour / Event text (pop-ups, logs and status texts)
10100030 | Power up | Texts regarding system behaviour / Event text (pop-ups, logs and status texts)
10200000 | Waiting for software ... | Texts regarding system behaviour / Event text (pop-ups, logs and status texts)
10200001 | Not possible Waiting for software ... | Texts regarding system behaviour / Event text (pop-ups, logs and status texts)
10300000 | Parameter | Texts regarding system behaviour / Parameter configuration (selected from a list)
10300001 | External | Texts regarding system behaviour / Parameter configuration (selected from a list)
10300002 | External -> Off | Texts regarding system behaviour / Parameter configuration (selected from a list)
10300003 | External -> Parameter | Texts regarding system behaviour / Parameter configuration (selected from a list)
11000000 | Start prepare | Texts related to engine operations / Timer text
11000010 | Crank on | Texts related to engine operations / Timer text
11000020 | Crank off | Texts related to engine operations / Timer text
11000030 | Run coil before crank | Texts related to engine operations / Timer text
11000040 | During start attempts | Texts related to engine operations / Parameter name
11000050 | Extended start prepare | Texts related to engine operations / Timer text
11000060 | Cooldown time | Texts related to engine operations / Timer text
11000070 | Temperature threshold | Texts related to engine operations / Parameter name
11000080 | Extended stop | Texts related to engine operations / Timer text
11000090 | Suppress alarm action | Texts related to engine operations / Timer text
11000100 | Stop failure | Texts related to engine operations / Alarm text (pop-ups and logs)
11000110 | Start failure | Texts related to engine operations / Alarm text (pop-ups and logs)
11000120 | Crank failure | Texts related to engine operations / Alarm text (pop-ups and logs)
11000130 | Total | Texts related to engine operations / An assignable function (CustomLogic)
11000140 | Overspeed 1 | Texts related to engine operations / Alarm text (pop-ups and logs)
11000150 | Overspeed 2 | Texts related to engine operations / Alarm text (pop-ups and logs)
11000160 | Under-speed 1 | Texts related to engine operations / Alarm text (pop-ups and logs)
11000170 | Under-speed 2 | Texts related to engine operations / Alarm text (pop-ups and logs)
11000180 | Magnetic pickup wire break alarm | Texts related to engine operations / Alarm text (pop-ups and logs)
11000190 | Externally stopped | Texts related to engine operations / Alarm text (pop-ups and logs)
11000200 | Externally started | Texts related to engine operations / Alarm text (pop-ups and logs)
11000210 | Normal | Texts related to engine operations / Parameter name
11000220 | Suppress alarm action | Texts related to engine operations / Parameter name
11000230 | During crank off | Texts related to engine operations / Parameter name
11000240 | Run coil on | Texts related to engine operations / Parameter name
11000250 | Since reset | Texts related to engine operations / An assignable function (CustomLogic)
11000260 | Faults | Texts related to engine operations / An assignable function (CustomLogic)
11000270 | Run detection not reached | Texts related to engine operations / Alarm text (pop-ups and logs)
11001000 | Oil pressure 1 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001010 | Oil pressure 2 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001020 | Oil temperature 1 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001030 | Oil temperature 2 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001040 | Coolant temperature 1 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001050 | Coolant temperature 2 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001060 | Coolant temperature 3 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001070 | Coolant pressure 1 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001080 | Coolant pressure 2 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001090 | Coolant pressure 3 | Texts related to engine operations / Alarm text (pop-ups and logs)
11001500 | Enable | Texts related to engine operations / Parameter name
11001510 | Keep stop coil active | Texts related to engine operations / Parameter name
11001520 | Number of configured stand-alone alarms is too high | Texts related to engine operations / Alarm text (pop-ups and logs)
11001530 | EIM3.1 hardware revision does not support stand-alone | Texts related to engine operations / Alarm text (pop-ups and logs)
11001540 | EIM3.1 safety shutdown still has control | Texts related to engine operations / Alarm text (pop-ups and logs)
11001550 | EIM3.1 safety shutdown configuration is not correct | Texts related to engine operations / Alarm text (pop-ups and logs)
11070000 | Engine run feedback lost | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070010 | Engine ready to start | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070020 | Engine not ready to start | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070030 | Engine cranking | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070040 | Engine running | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070050 | Engine cooldown | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070060 | Engine stopping | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070070 | Engine idle run | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070080 | Engine start blocked | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070090 | Engine start not blocked | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070100 | Engine cooldown aborted | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11070110 | Engine externally stopped | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11080000 | Run coil | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080001 | Stop coil | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080002 | Start prepare | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080003 | Crank | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080004 | Engine coolant water | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080005 | Stop failure | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080006 | Start failure | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080007 | Crank failure | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080008 | Overspeed 1 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080009 | Overspeed 2 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080010 | Under-speed 1 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080011 | Under-speed 2 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080012 | Magnetic pickup wire break alarm | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080013 | Engine state | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080014 | Engine start requested | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080015 | Engine stop requested | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080016 | Engine start blocked | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080017 | Engine stop blocked | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080018 | Engine abort and lock operations | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080019 | Externally stopped | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080020 | Externally started | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080021 | Not ready to start | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080022 | Ready to start | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080023 | Starting | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080024 | Cooldown | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080025 | Engine emergency stop requested | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080026 | Engine forced stop requested | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080027 | Stopping | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080028 | Extended stop | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080029 | Oil pressure 1 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080030 | Oil pressure 2 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080031 | Engine oil temperature | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080032 | Oil temperature 1 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080033 | Oil temperature 2 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080034 | Coolant temperature 1 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080035 | Coolant temperature 2 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080036 | Coolant temperature 3 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080037 | Coolant level 1 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080038 | Coolant level 2 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080039 | Coolant level 3 | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080040 | Engine coolant level | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080041 | Start prepare completed | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080042 | Engine oil pressure | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080043 | Engine oil temperature | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080044 | Engine coolant water | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080045 | Engine coolant level | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080046 | Engine speed | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080048 | Crank delay | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080049 | Warm up delay | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080050 | Cooldown abort | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080051 | De-load genset | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11080100 | Manual reset | Texts related to engine operations / Parameter name
11080101 | Status OK | Texts related to engine operations / Parameter name
11090000 | Follow crank | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090001 | Always on | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090002 | Activated | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090003 | Not activated | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090004 | Engine stopping | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090005 | Engine running low speed | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090006 | Ready for operation | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090007 | Not ready for operation | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090008 | Start enable not activated | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090009 | Engine stopping | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090010 | Engine already running | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090011 | Engine already stopped | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090012 | GB position is unknown | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090013 | GB operation in progress | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090014 | Engine running | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090015 | Emergency supply | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090016 | Engine starting | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090017 | Preparing | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11090020 | Shutdown override | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11100000 | Enable | Texts related to engine operations / Parameter name
11100010 | Delay | Texts related to engine operations / Timer text
11100100 | Use | Texts related to engine operations / Parameter name
11100110 | Delay | Texts related to engine operations / Timer text
11100200 | Use | Texts related to engine operations / Parameter name
11100210 | Set point | Texts related to engine operations / Parameter name
11100300 | Use | Texts related to engine operations / Parameter name
11100310 | Set point | Texts related to engine operations / Parameter name
11100400 | Use | Texts related to engine operations / Parameter name
11110000 | Enable | Texts related to engine operations / Parameter name
11110010 | Delay | Texts related to engine operations / Timer text
11110100 | Use | Texts related to engine operations / Parameter name
11110110 | Delay | Texts related to engine operations / Timer text
11110200 | Use | Texts related to engine operations / Parameter name
11110210 | Set point | Texts related to engine operations / Parameter name
11110300 | Use | Texts related to engine operations / Parameter name
11110310 | Set point | Texts related to engine operations / Parameter name
11110400 | Use | Texts related to engine operations / Parameter name
11120000 | Extended inhibit | Texts related to engine operations / Timer text
11170000 | Idle run started | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11170010 | Idle run completed | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11170020 | Idle run aborted | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11170030 | Idle run started | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11170040 | Idle run completed | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11170050 | Idle run aborted | Texts related to engine operations / Event text (pop-ups, logs and status texts)
11180000 | Idling | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11180001 | Idle run | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11180002 | End idle start | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11180003 | End idle stop | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11180004 | Low speed | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11180005 | Temperature control | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11190000 | Idle run start active | Texts related to engine operations / Miscellaneous text (various uses)
11190010 | Idle run stop active | Texts related to engine operations / Miscellaneous text (various uses)
11190011 | Idle run | Texts related to engine operations / Miscellaneous text (various uses)
11200000 | RPM | Texts related to engine operations / Parameter name
11200010 | Frequency | Texts related to engine operations / Parameter name
11200020 | Oil pressure | Texts related to engine operations / Parameter name
11200030 | Primary running feedback | Texts related to engine operations / Parameter name
11200040 | Delay | Texts related to engine operations / Timer text
11200050 | Primary running feedback failure | Texts related to engine operations / Alarm text (pop-ups and logs)
11200060 | Disengage crank | Texts related to engine operations / Parameter name
11200070 | Number of MPU teeth | Texts related to engine operations / Parameter name
11200080 | Use magnetic pickup | Texts related to engine operations / Parameter name
11200090 | Use oil pressure | Texts related to engine operations / Parameter name
11200100 | Use engine speed | Texts related to engine operations / Parameter name
11210000 | RPM running detected | Texts related to engine operations / Miscellaneous text (various uses)
11210010 | RPM zero | Texts related to engine operations / Miscellaneous text (various uses)
11210020 | RPM remove starter | Texts related to engine operations / Miscellaneous text (various uses)
11210030 | Run detection not reached | Texts related to engine operations / Miscellaneous text (various uses)
11280000 | Engine oil pressure | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11280001 | Engine MPU | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11280002 | Digital running detection | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11280003 | Remove start (release crank relay) | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11280004 | Primary running feedback failure | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11280005 | Running | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11280006 | Not running | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11290000 | Digital input | Texts related to engine operations / Parameter name
11290001 | Engine speed | Texts related to engine operations / Parameter name
11290002 | Frequency | Texts related to engine operations / Parameter name
11290004 | Oil pressure | Texts related to engine operations / Parameter name
11300000 | Total running hours | Texts related to engine operations / An assignable function (CustomLogic)
11300010 | Total running minutes | Texts related to engine operations / An assignable function (CustomLogic)
11300020 | Total running hours notification | Texts related to engine operations / Alarm text (pop-ups and logs)
11300330 | Service timer 1 | Texts related to engine operations / Alarm text (pop-ups and logs)
11300340 | Service timer 2 | Texts related to engine operations / Alarm text (pop-ups and logs)
11300350 | Service timer 3 | Texts related to engine operations / Alarm text (pop-ups and logs)
11300360 | Service timer 4 | Texts related to engine operations / Alarm text (pop-ups and logs)
11300370 | Running hours load profiled | Texts related to engine operations / An assignable function (CustomLogic)
11300380 | Running minutes shutdown override | Texts related to engine operations / An assignable function (CustomLogic)
11300390 | Running hours shutdown override | Texts related to engine operations / An assignable function (CustomLogic)
11300440 | Trip running hours | Texts related to engine operations / An assignable function (CustomLogic)
11380000 | Total running hours notification | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11380002 | Hours until total running hours notification | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11390000 | Running hours since reset %s | Texts related to engine operations / An assignable function (CustomLogic)
11390001 | Running minutes since reset %s | Texts related to engine operations / An assignable function (CustomLogic)
11390002 | Trip running hours %s notification | Texts related to engine operations / Alarm text (pop-ups and logs)
11390003 | Trip running hours %s notification | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11390004 | Hours until trip running hours %s notification | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11390005 | Running days since reset %s | Texts related to engine operations / An assignable function (CustomLogic)
11390006 | Running hours relative | Texts related to engine operations / An assignable function (CustomLogic)
11390007 | Relative | Texts related to engine operations / Miscellaneous text (various uses)
11390008 | Total | Texts related to engine operations / Miscellaneous text (various uses)
11390009 | Load profiled | Texts related to engine operations / Miscellaneous text (various uses)
11400000 | Enable | Texts related to engine operations / Parameter name
11400010 | OFF timer | Texts related to engine operations / Parameter name
11400020 | ON timer | Texts related to engine operations / Parameter name
11480000 | Priming | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11500000 | Pump ON set point | Texts related to engine operations / Parameter name
11500010 | Pump OFF set point | Texts related to engine operations / Parameter name
11500030 | Fuel fill failure | Texts related to engine operations / Alarm text (pop-ups and logs)
11500040 | Pump ON delay | Texts related to engine operations / Timer text
11500050 | Pump OFF delay | Texts related to engine operations / Timer text
11580000 | Fuel level | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11580001 | Fuel pump | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11580002 | Fuel fill failure | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11580003 | Activate fuel pump logic | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11580004 | Deactivate fuel pump logic | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
11580005 | Fuel level | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
12000000 | Start enable removed during start | Texts related to engine operations / Alarm text (pop-ups and logs)
12070000 | Engine start requested | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070010 | Engine stop requested | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070020 | Start enable activated | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070030 | Start enable deactivated | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070040 | Idle run activated | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070050 | Idle run deactivated | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070080 | Engine start block requested | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070090 | Engine start unblock requested | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070100 | Engine stop block requested | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12070110 | Engine stop unblock requested | Texts related to engine operations / Event text (pop-ups, logs and status texts)
12080001 | Start enable | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
12080002 | Force idle run | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
12080003 | Start enable removed during start | Texts related to engine operations / Assignable function (input/output config menus, Modbus)
13000000 | Allow start when | Texts related to inverter operations / Miscellaneous text (various uses)
13000010 | Allow stop when | Texts related to inverter operations / Miscellaneous text (various uses)
13000020 | Allow breaker close when | Texts related to inverter operations / Miscellaneous text (various uses)
13000030 | Allow breaker open when | Texts related to inverter operations / Miscellaneous text (various uses)
13070040 | Inverter start blocked | Texts related to inverter operations / Event text (pop-ups, logs and status texts)
13070050 | Inverter start not blocked | Texts related to inverter operations / Event text (pop-ups, logs and status texts)
13080000 | Inverter state | Texts related to inverter operations / Assignable function (input/output config menus, Modbus)
13080001 | Inverter start requested | Texts related to inverter operations / Assignable function (input/output config menus, Modbus)
13080002 | Inverter stop requested | Texts related to inverter operations / Assignable function (input/output config menus, Modbus)
13080003 | Run | Texts related to inverter operations / Assignable function (input/output config menus, Modbus)
13080004 | Stop | Texts related to inverter operations / Assignable function (input/output config menus, Modbus)
13080005 | Start | Texts related to inverter operations / Assignable function (input/output config menus, Modbus)
13090010 | Start on | Texts related to inverter operations / Timer text
13090100 | Inverter ready for operation | Texts related to inverter operations / Label text
13090101 | Inverter running | Texts related to inverter operations / Label text
13090102 | Inverter stopping | Texts related to inverter operations / Label text
13090103 | Inverter starting | Texts related to inverter operations / Label text
13090104 | Inverter already running | Texts related to inverter operations / Label text
13090105 | Inverter already stopped | Texts related to inverter operations / Label text
13090106 | De-loading inverter | Texts related to inverter operations / Label text
13090110 | Inverter is started | Texts related to inverter operations / Label text
13090111 | Inverter is stopped | Texts related to inverter operations / Label text
13090112 | Inverter in any state | Texts related to inverter operations / Label text
13090113 | Inverter is not started | Texts related to inverter operations / Label text
13090114 | Inverter is not stopped | Texts related to inverter operations / Label text
13090120 | Breaker is open | Texts related to inverter operations / Label text
13090121 | Breaker is closed | Texts related to inverter operations / Label text
13090122 | Breaker in any state | Texts related to inverter operations / Label text
13090123 | Breaker is not open | Texts related to inverter operations / Label text
13090124 | Breaker is not closed | Texts related to inverter operations / Label text
20000000 | Breaker type has changed | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20000100 | Breaker closed | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20000110 | Breaker opened | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20000120 | Breaker de-loading | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20000130 | Breaker synchronising | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20000140 | Breaker close requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20000150 | Breaker open requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20000160 | Breaker trip requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20000170 | Breaker preparing | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20005000 | Continuous breaker | Texts related to breaker operations / Parameter configuration (selected from a list)
20005001 | Pulse breaker | Texts related to breaker operations / Parameter configuration (selected from a list)
20005002 | Compact breaker | Texts related to breaker operations / Parameter configuration (selected from a list)
20005010 | De-loading breaker | Texts related to breaker operations / Parameter configuration (selected from a list)
20005011 | Synchronising breaker | Texts related to breaker operations / Parameter configuration (selected from a list)
20005020 | Breaker is closed | Texts related to breaker operations / Parameter configuration (selected from a list)
20005021 | Breaker is open | Texts related to breaker operations / Parameter configuration (selected from a list)
20005022 | Breaker closing failure | Texts related to breaker operations / Parameter configuration (selected from a list)
20005023 | Breaker opening failure | Texts related to breaker operations / Parameter configuration (selected from a list)
20005024 | Breaker position failure | Texts related to breaker operations / Parameter configuration (selected from a list)
20005050 | Under-voltage coil | Texts related to breaker operations / Parameter configuration (selected from a list)
20010000 | GB closed | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010010 | GB opened | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010020 | GB de-loading | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010030 | GB synchronising | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010040 | GB close requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010050 | GB open requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010060 | GB trip requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010070 | GB preparing | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010090 | GB racked out on | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20010100 | GB racked out off | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20015000 | Breaker type | Texts related to breaker operations / Miscellaneous text (various uses)
20015001 | Pulse time ON | Texts related to breaker operations / Miscellaneous text (various uses)
20015002 | Pulse time OFF | Texts related to breaker operations / Miscellaneous text (various uses)
20015003 | Spring load time | Texts related to breaker operations / Miscellaneous text (various uses)
20015004 | GB closing failure | Texts related to breaker operations / Miscellaneous text (various uses)
20015005 | GB opening failure | Texts related to breaker operations / Miscellaneous text (various uses)
20015006 | GB position failure | Texts related to breaker operations / Miscellaneous text (various uses)
20015007 | GB configuration failure | Texts related to breaker operations / Miscellaneous text (various uses)
20015008 | GB synchronisation failure | Texts related to breaker operations / Miscellaneous text (various uses)
20015009 | GB de-load failure | Texts related to breaker operations / Miscellaneous text (various uses)
20015010 | GB closed | Texts related to breaker operations / Miscellaneous text (various uses)
20015011 | GB open | Texts related to breaker operations / Miscellaneous text (various uses)
20015012 | GB close | Texts related to breaker operations / Miscellaneous text (various uses)
20015013 | GB open | Texts related to breaker operations / Miscellaneous text (various uses)
20015014 | GB is spring loaded | Texts related to breaker operations / Miscellaneous text (various uses)
20015015 | Synchronising GB | Texts related to breaker operations / Miscellaneous text (various uses)
20015016 | De-loading GB | Texts related to breaker operations / Miscellaneous text (various uses)
20015017 | Open point (de-loading) | Texts related to breaker operations / Miscellaneous text (various uses)
20015018 | GB tripped (external) | Texts related to breaker operations / Miscellaneous text (various uses)
20015019 | GB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20015020 | GB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20015021 | GB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20015022 | GB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20015023 | GB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20015024 | GB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20015025 | GB operations | Texts related to breaker operations / Miscellaneous text (various uses)
20015026 | GB state | Texts related to breaker operations / Miscellaneous text (various uses)
20015027 | GB open blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20015028 | GB close blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20015029 | GB direct open request | Texts related to breaker operations / Miscellaneous text (various uses)
20015030 | GB direct close request | Texts related to breaker operations / Miscellaneous text (various uses)
20015031 | GB sync request | Texts related to breaker operations / Miscellaneous text (various uses)
20015032 | GB de-load request | Texts related to breaker operations / Miscellaneous text (various uses)
20015033 | GB abort and lock operations | Texts related to breaker operations / Miscellaneous text (various uses)
20015034 | GB trips | Texts related to breaker operations / Miscellaneous text (various uses)
20015035 | GB is preparing | Texts related to breaker operations / Miscellaneous text (various uses)
20015036 | GB trip | Texts related to breaker operations / Miscellaneous text (various uses)
20015500 | GB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20015501 | GB is opening | Texts related to breaker operations / Miscellaneous text (various uses)
20015502 | GB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20015503 | GB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20015504 | GB is closing | Texts related to breaker operations / Miscellaneous text (various uses)
20015505 | GB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20015506 | Voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20015507 | Engine not running | Texts related to breaker operations / Miscellaneous text (various uses)
20015508 | Busbar voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20015509 | Not possible while GB is in operation | Texts related to breaker operations / Miscellaneous text (various uses)
20015510 | GB cannot close when TB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20020000 | SGB closed | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20020010 | SGB opened | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20020020 | SGB de-loading | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20020030 | SGB synchronising | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20020040 | SGB close requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20020050 | SGB open requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20020060 | SGB trip requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20020070 | SGB preparing | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20025000 | Breaker type | Texts related to breaker operations / Miscellaneous text (various uses)
20025001 | Pulse time ON | Texts related to breaker operations / Miscellaneous text (various uses)
20025002 | Pulse time OFF | Texts related to breaker operations / Miscellaneous text (various uses)
20025003 | Spring-load time | Texts related to breaker operations / Miscellaneous text (various uses)
20025004 | SGB closing failure | Texts related to breaker operations / Miscellaneous text (various uses)
20025005 | SGB opening failure | Texts related to breaker operations / Miscellaneous text (various uses)
20025006 | SGB position failure | Texts related to breaker operations / Miscellaneous text (various uses)
20025007 | SGB configuration failure | Texts related to breaker operations / Miscellaneous text (various uses)
20025008 | SGB synchronisation failure | Texts related to breaker operations / Miscellaneous text (various uses)
20025009 | SGB de-load failure | Texts related to breaker operations / Miscellaneous text (various uses)
20025010 | SGB closed | Texts related to breaker operations / Miscellaneous text (various uses)
20025011 | SGB open | Texts related to breaker operations / Miscellaneous text (various uses)
20025012 | SGB close | Texts related to breaker operations / Miscellaneous text (various uses)
20025013 | SGB open | Texts related to breaker operations / Miscellaneous text (various uses)
20025014 | SGB is spring loaded | Texts related to breaker operations / Miscellaneous text (various uses)
20025015 | Synchronising SGB | Texts related to breaker operations / Miscellaneous text (various uses)
20025016 | De-loading SGB | Texts related to breaker operations / Miscellaneous text (various uses)
20025017 | Open point (de-loading) | Texts related to breaker operations / Miscellaneous text (various uses)
20025018 | SGB tripped (external) | Texts related to breaker operations / Miscellaneous text (various uses)
20025019 | SGB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20025020 | SGB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20025021 | SGB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20025022 | SGB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20025023 | SGB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20025024 | SGB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20025025 | SGB operations | Texts related to breaker operations / Miscellaneous text (various uses)
20025026 | SGB state | Texts related to breaker operations / Miscellaneous text (various uses)
20025027 | SGB open blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20025028 | SGB close blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20025029 | SGB direct open request | Texts related to breaker operations / Miscellaneous text (various uses)
20025030 | SGB direct close request | Texts related to breaker operations / Miscellaneous text (various uses)
20025031 | SGB sync request | Texts related to breaker operations / Miscellaneous text (various uses)
20025032 | SGB de-load request | Texts related to breaker operations / Miscellaneous text (various uses)
20025033 | SGB abort and lock operations | Texts related to breaker operations / Miscellaneous text (various uses)
20025034 | SGB trips | Texts related to breaker operations / Miscellaneous text (various uses)
20025035 | SGB is preparing | Texts related to breaker operations / Miscellaneous text (various uses)
20025036 | SGB trip | Texts related to breaker operations / Miscellaneous text (various uses)
20025500 | SGB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20025501 | SGB is opening | Texts related to breaker operations / Miscellaneous text (various uses)
20025502 | SGB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20025503 | SGB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20025504 | SGB is closing | Texts related to breaker operations / Miscellaneous text (various uses)
20025505 | SGB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20025506 | Voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20025507 | Infinite sync active | Texts related to breaker operations / Miscellaneous text (various uses)
20025508 | Busbar voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20030000 | BTB closed | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030010 | BTB opened | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030020 | BTB de-loading | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030030 | BTB synchronising | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030040 | BTB close requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030050 | BTB open requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030060 | BTB trip requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030070 | BTB preparing | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030080 | BTB tripped externally | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030090 | BTB racked out on | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20030100 | BTB racked out off | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20035000 | Breaker type | Texts related to breaker operations / Miscellaneous text (various uses)
20035001 | Pulse time ON | Texts related to breaker operations / Miscellaneous text (various uses)
20035002 | Pulse time OFF | Texts related to breaker operations / Miscellaneous text (various uses)
20035003 | Spring load time | Texts related to breaker operations / Miscellaneous text (various uses)
20035004 | BTB closing failure | Texts related to breaker operations / Miscellaneous text (various uses)
20035005 | BTB opening failure | Texts related to breaker operations / Miscellaneous text (various uses)
20035006 | BTB position failure | Texts related to breaker operations / Miscellaneous text (various uses)
20035007 | BTB configuration failure | Texts related to breaker operations / Miscellaneous text (various uses)
20035008 | BTB synchronisation failure | Texts related to breaker operations / Miscellaneous text (various uses)
20035009 | BTB de-load failure | Texts related to breaker operations / Miscellaneous text (various uses)
20035010 | BTB closed | Texts related to breaker operations / Miscellaneous text (various uses)
20035011 | BTB open | Texts related to breaker operations / Miscellaneous text (various uses)
20035012 | BTB close | Texts related to breaker operations / Miscellaneous text (various uses)
20035013 | BTB open | Texts related to breaker operations / Miscellaneous text (various uses)
20035014 | BTB is spring loaded | Texts related to breaker operations / Miscellaneous text (various uses)
20035015 | Synchronising BTB | Texts related to breaker operations / Miscellaneous text (various uses)
20035016 | De-loading BTB | Texts related to breaker operations / Miscellaneous text (various uses)
20035017 | Open point (de-loading) | Texts related to breaker operations / Miscellaneous text (various uses)
20035018 | BTB tripped (external) | Texts related to breaker operations / Miscellaneous text (various uses)
20035019 | BTB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20035020 | BTB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20035021 | BTB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20035022 | BTB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20035023 | BTB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20035024 | BTB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20035025 | BTB operations | Texts related to breaker operations / Miscellaneous text (various uses)
20035026 | BTB state | Texts related to breaker operations / Miscellaneous text (various uses)
20035027 | BTB open blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20035028 | BTB close blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20035029 | BTB direct open request | Texts related to breaker operations / Miscellaneous text (various uses)
20035030 | BTB direct close request | Texts related to breaker operations / Miscellaneous text (various uses)
20035031 | BTB sync request | Texts related to breaker operations / Miscellaneous text (various uses)
20035032 | BTB de-load request | Texts related to breaker operations / Miscellaneous text (various uses)
20035033 | BTB abort and lock operations | Texts related to breaker operations / Miscellaneous text (various uses)
20035034 | BTB trips | Texts related to breaker operations / Miscellaneous text (various uses)
20035035 | BTB is preparing | Texts related to breaker operations / Miscellaneous text (various uses)
20035036 | BTB trip | Texts related to breaker operations / Miscellaneous text (various uses)
20035500 | BTB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20035501 | BTB is opening | Texts related to breaker operations / Miscellaneous text (various uses)
20035502 | Dividing section | Texts related to breaker operations / Miscellaneous text (various uses)
20035503 | BTB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20035504 | BTB is closing | Texts related to breaker operations / Miscellaneous text (various uses)
20035505 | Synchronising sections | Texts related to breaker operations / Miscellaneous text (various uses)
20035506 | Busbar A voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20035507 | Busbar B voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20035508 | Waiting for another close operation | Texts related to breaker operations / Miscellaneous text (various uses)
20035509 | BTB dividing section | Texts related to breaker operations / Miscellaneous text (various uses)
20040000 | SCB closed | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20040010 | SCB opened | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20040020 | SCB de-loading | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20040030 | SCB synchronising | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20040040 | SCB close requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20040050 | SCB open requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20040060 | SCB trip requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20040070 | SCB preparing | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20045000 | Breaker type | Texts related to breaker operations / Miscellaneous text (various uses)
20045001 | Pulse time ON | Texts related to breaker operations / Miscellaneous text (various uses)
20045002 | Pulse time OFF | Texts related to breaker operations / Miscellaneous text (various uses)
20045003 | Spring load time | Texts related to breaker operations / Miscellaneous text (various uses)
20045004 | SCB closing failure | Texts related to breaker operations / Miscellaneous text (various uses)
20045005 | SCB opening failure | Texts related to breaker operations / Miscellaneous text (various uses)
20045006 | SCB position failure | Texts related to breaker operations / Miscellaneous text (various uses)
20045007 | SCB configuration failure | Texts related to breaker operations / Miscellaneous text (various uses)
20045008 | SCB synchronisation failure | Texts related to breaker operations / Miscellaneous text (various uses)
20045009 | SCB de-load failure | Texts related to breaker operations / Miscellaneous text (various uses)
20045010 | SCB closed | Texts related to breaker operations / Miscellaneous text (various uses)
20045011 | SCB open | Texts related to breaker operations / Miscellaneous text (various uses)
20045012 | SCB close | Texts related to breaker operations / Miscellaneous text (various uses)
20045013 | SCB open | Texts related to breaker operations / Miscellaneous text (various uses)
20045014 | SCB is spring loaded | Texts related to breaker operations / Miscellaneous text (various uses)
20045015 | Synchronising SCB | Texts related to breaker operations / Miscellaneous text (various uses)
20045016 | De-loading SCB | Texts related to breaker operations / Miscellaneous text (various uses)
20045017 | Open point (de-loading) | Texts related to breaker operations / Miscellaneous text (various uses)
20045018 | SCB tripped (external) | Texts related to breaker operations / Miscellaneous text (various uses)
20045019 | SCB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20045020 | SCB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20045021 | SCB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20045022 | SCB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20045023 | SCB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20045024 | SCB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20045025 | SCB operations | Texts related to breaker operations / Miscellaneous text (various uses)
20045026 | SCB state | Texts related to breaker operations / Miscellaneous text (various uses)
20045027 | SCB open blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20045028 | SCB close blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20045029 | SCB direct open request | Texts related to breaker operations / Miscellaneous text (various uses)
20045030 | SCB direct close request | Texts related to breaker operations / Miscellaneous text (various uses)
20045031 | SCB sync request | Texts related to breaker operations / Miscellaneous text (various uses)
20045032 | SCB de-load request | Texts related to breaker operations / Miscellaneous text (various uses)
20045033 | SCB abort and lock operations | Texts related to breaker operations / Miscellaneous text (various uses)
20045034 | SCB trips | Texts related to breaker operations / Miscellaneous text (various uses)
20045035 | SCB is preparing | Texts related to breaker operations / Miscellaneous text (various uses)
20045036 | SCB trip | Texts related to breaker operations / Miscellaneous text (various uses)
20045500 | SCB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20045501 | SCB is opening | Texts related to breaker operations / Miscellaneous text (various uses)
20045502 | SCB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20045503 | SCB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20045504 | SCB is closing | Texts related to breaker operations / Miscellaneous text (various uses)
20045505 | SCB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20045506 | Shore connection V/Hz not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20045507 | Infinite sync active | Texts related to breaker operations / Miscellaneous text (various uses)
20045508 | Busbar V/Hz not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20050000 | TB closed | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050010 | TB opened | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050020 | TB de-loading | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050030 | TB synchronising | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050040 | TB close requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050050 | TB open requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050060 | TB trip requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050070 | TB preparing | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050080 | TB tripped externally | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050090 | TB racked out on | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20050100 | TB racked out off | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20055000 | Breaker type | Texts related to breaker operations / Miscellaneous text (various uses)
20055001 | Pulse time ON | Texts related to breaker operations / Miscellaneous text (various uses)
20055002 | Pulse time OFF | Texts related to breaker operations / Miscellaneous text (various uses)
20055003 | Spring-load time | Texts related to breaker operations / Miscellaneous text (various uses)
20055004 | TB closing failure | Texts related to breaker operations / Miscellaneous text (various uses)
20055005 | TB opening failure | Texts related to breaker operations / Miscellaneous text (various uses)
20055006 | TB position failure | Texts related to breaker operations / Miscellaneous text (various uses)
20055007 | TB configuration failure | Texts related to breaker operations / Miscellaneous text (various uses)
20055008 | TB synchronisation failure | Texts related to breaker operations / Miscellaneous text (various uses)
20055009 | TB de-load failure | Texts related to breaker operations / Miscellaneous text (various uses)
20055010 | TB closed | Texts related to breaker operations / Miscellaneous text (various uses)
20055011 | TB open | Texts related to breaker operations / Miscellaneous text (various uses)
20055012 | TB close | Texts related to breaker operations / Miscellaneous text (various uses)
20055013 | TB open | Texts related to breaker operations / Miscellaneous text (various uses)
20055014 | TB is spring loaded | Texts related to breaker operations / Miscellaneous text (various uses)
20055015 | Synchronising TB | Texts related to breaker operations / Miscellaneous text (various uses)
20055016 | De-loading TB | Texts related to breaker operations / Miscellaneous text (various uses)
20055017 | Open point (de-loading) | Texts related to breaker operations / Miscellaneous text (various uses)
20055018 | TB tripped (external) | Texts related to breaker operations / Miscellaneous text (various uses)
20055019 | TB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20055020 | TB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20055021 | TB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20055022 | TB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20055023 | TB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20055024 | TB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20055025 | TB operations | Texts related to breaker operations / Miscellaneous text (various uses)
20055026 | TB state | Texts related to breaker operations / Miscellaneous text (various uses)
20055027 | TB open blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20055028 | TB close blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20055029 | TB direct open request | Texts related to breaker operations / Miscellaneous text (various uses)
20055030 | TB direct close request | Texts related to breaker operations / Miscellaneous text (various uses)
20055031 | TB sync request | Texts related to breaker operations / Miscellaneous text (various uses)
20055032 | TB de-load request | Texts related to breaker operations / Miscellaneous text (various uses)
20055033 | TB abort and lock operations | Texts related to breaker operations / Miscellaneous text (various uses)
20055034 | TB trips | Texts related to breaker operations / Miscellaneous text (various uses)
20055035 | TB is preparing | Texts related to breaker operations / Miscellaneous text (various uses)
20055036 | TB trip | Texts related to breaker operations / Miscellaneous text (various uses)
20055500 | TB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20055501 | TB is opening | Texts related to breaker operations / Miscellaneous text (various uses)
20055502 | TB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20055503 | TB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20055504 | TB is closing | Texts related to breaker operations / Miscellaneous text (various uses)
20055505 | TB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20055506 | Busbar B voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20055507 | TB cannot open, GB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20055508 | TB cannot open, EDG is not ready | Texts related to breaker operations / Miscellaneous text (various uses)
20055509 | Not possible, TB is in operation | Texts related to breaker operations / Miscellaneous text (various uses)
20055510 | TB cannot open, GB not ready | Texts related to breaker operations / Miscellaneous text (various uses)
20055511 | TB blocked by MB | Texts related to breaker operations / Miscellaneous text (various uses)
20060000 | MB closed | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060010 | MB opened | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060020 | MB de-loading | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060030 | MB synchronising | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060040 | MB close requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060050 | MB open requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060060 | MB trip requested | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060070 | MB preparing | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060080 | MB tripped externally | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060090 | MB racked out on | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060100 | MB racked out off | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20060110 | External MB open failure | Texts related to breaker operations / Event text (pop-ups, logs and status texts)
20065000 | Breaker type | Texts related to breaker operations / Miscellaneous text (various uses)
20065001 | Pulse time ON | Texts related to breaker operations / Miscellaneous text (various uses)
20065002 | Pulse time OFF | Texts related to breaker operations / Miscellaneous text (various uses)
20065003 | Spring-load time | Texts related to breaker operations / Miscellaneous text (various uses)
20065004 | MB closing failure | Texts related to breaker operations / Miscellaneous text (various uses)
20065005 | MB opening failure | Texts related to breaker operations / Miscellaneous text (various uses)
20065006 | MB position failure | Texts related to breaker operations / Miscellaneous text (various uses)
20065007 | MB configuration failure | Texts related to breaker operations / Miscellaneous text (various uses)
20065008 | MB synchronisation failure | Texts related to breaker operations / Miscellaneous text (various uses)
20065009 | MB de-load failure | Texts related to breaker operations / Miscellaneous text (various uses)
20065010 | MB closed | Texts related to breaker operations / Miscellaneous text (various uses)
20065011 | MB open | Texts related to breaker operations / Miscellaneous text (various uses)
20065012 | MB close | Texts related to breaker operations / Miscellaneous text (various uses)
20065013 | MB open | Texts related to breaker operations / Miscellaneous text (various uses)
20065014 | MB is spring loaded | Texts related to breaker operations / Miscellaneous text (various uses)
20065015 | Synchronising MB | Texts related to breaker operations / Miscellaneous text (various uses)
20065016 | De-loading MB | Texts related to breaker operations / Miscellaneous text (various uses)
20065017 | Open point (de-loading) | Texts related to breaker operations / Miscellaneous text (various uses)
20065018 | MB tripped (external) | Texts related to breaker operations / Miscellaneous text (various uses)
20065019 | MB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20065020 | MB short circuit | Texts related to breaker operations / Miscellaneous text (various uses)
20065021 | MB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20065022 | MB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20065023 | MB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20065024 | MB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20065025 | MB operations | Texts related to breaker operations / Miscellaneous text (various uses)
20065026 | MB state | Texts related to breaker operations / Miscellaneous text (various uses)
20065027 | MB open blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20065028 | MB close blocked | Texts related to breaker operations / Miscellaneous text (various uses)
20065029 | MB direct open request | Texts related to breaker operations / Miscellaneous text (various uses)
20065030 | MB direct close request | Texts related to breaker operations / Miscellaneous text (various uses)
20065031 | MB sync request | Texts related to breaker operations / Miscellaneous text (various uses)
20065032 | MB de-load request | Texts related to breaker operations / Miscellaneous text (various uses)
20065033 | MB abort and lock operations | Texts related to breaker operations / Miscellaneous text (various uses)
20065034 | MB trips | Texts related to breaker operations / Miscellaneous text (various uses)
20065035 | MB configuration failure | Texts related to breaker operations / Miscellaneous text (various uses)
20065036 | MB is preparing | Texts related to breaker operations / Miscellaneous text (various uses)
20065037 | MB trip | Texts related to breaker operations / Miscellaneous text (various uses)
20065500 | MB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20065501 | MB is opening | Texts related to breaker operations / Miscellaneous text (various uses)
20065502 | MB is de-loading | Texts related to breaker operations / Miscellaneous text (various uses)
20065503 | MB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20065504 | MB is closing | Texts related to breaker operations / Miscellaneous text (various uses)
20065505 | MB is synchronising | Texts related to breaker operations / Miscellaneous text (various uses)
20065506 | Mains voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20065507 | Busbar voltage/frequency not OK | Texts related to breaker operations / Miscellaneous text (various uses)
20065508 | MB cannot open, GB not ready | Texts related to breaker operations / Miscellaneous text (various uses)
20065509 | MB cannot open, DG is not ready | Texts related to breaker operations / Miscellaneous text (various uses)
20065510 | MB cannot open, GB is open | Texts related to breaker operations / Miscellaneous text (various uses)
20065511 | Not possible while MB is in operation | Texts related to breaker operations / Miscellaneous text (various uses)
20065512 | GB cannot close when MB is closed | Texts related to breaker operations / Miscellaneous text (various uses)
20065513 | MB is not present | Texts related to breaker operations / Miscellaneous text (various uses)
20100000 | Type | Texts related to breaker operations / Parameter name
20100010 | Pulse time ON | Texts related to breaker operations / Timer text
20100020 | Pulse time OFF | Texts related to breaker operations / Timer text
20100030 | Spring load time | Texts related to breaker operations / Timer text
20100040 | Breaker closing failure | Texts related to breaker operations / Alarm text (pop-ups and logs)
20100050 | Breaker opening failure | Texts related to breaker operations / Alarm text (pop-ups and logs)
20100060 | Breaker position failure | Texts related to breaker operations / Alarm text (pop-ups and logs)
20100070 | Breaker configuration failure | Texts related to breaker operations / Alarm text (pop-ups and logs)
20100080 | Breaker synchronisation failure | Texts related to breaker operations / Alarm text (pop-ups and logs)
20100090 | Breaker de-load failure | Texts related to breaker operations / Alarm text (pop-ups and logs)
20100100 | Close operations | Texts related to breaker operations / An assignable function (CustomLogic)
20100110 | Breaker open point (de-loading) | Texts related to breaker operations / Parameter name
20100120 | Breaker trip (external) | Texts related to breaker operations / Alarm text (pop-ups and logs)
20100130 | Breaker short circuit | Texts related to breaker operations / Alarm text (pop-ups and logs)
20100140 | Trips | Texts related to breaker operations / An assignable function (CustomLogic)
20100150 | Close operations since reset | Texts related to breaker operations / An assignable function (CustomLogic)
20100160 | Failed operations | Texts related to breaker operations / An assignable function (CustomLogic)
20180000 | Breaker open feedback | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180001 | Breaker closed feedback | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180002 | Breaker open | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180003 | Breaker close | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180004 | Breaker spring-loaded | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180005 | Breaker close failure | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180006 | Breaker open failure | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180007 | Breaker position failure | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180008 | Breaker configuration failure | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180009 | Breaker synchronisation failure | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180010 | Breaker de-load failure | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180011 | Breaker trip (external) | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180012 | Breaker short circuit | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180013 | Breaker short circuit | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180014 | Breaker is open | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180015 | Breaker is closed | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180016 | Breaker state | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180017 | Breaker open blocked | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180018 | Breaker close blocked | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180019 | Breaker direct open request | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180020 | Breaker direct close request | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180021 | Breaker sync. request | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180022 | Breaker de-load request | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180023 | Breaker abort and lock operations | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180024 | Breaker is synchronising | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180025 | Breaker is de-loading | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180026 | Breaker is preparing | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20180027 | Breaker trip | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
20200100 | Close operations | Texts related to breaker operations / Label text
20200140 | Trips | Texts related to breaker operations / Label text
20200150 | Close operations since reset | Texts related to breaker operations / An assignable function (CustomLogic)
20200160 | Failed operations | Texts related to breaker operations / An assignable function (CustomLogic)
25000000 | Tie breaker sync enabled | Texts related to breaker operations / Parameter name
25000010 | Tie breaker de-load enabled | Texts related to breaker operations / Parameter name
25000020 | Generator breaker transfer delay | Texts related to breaker operations / Timer text
25000030 | Tie breaker transfer delay | Texts related to breaker operations / Timer text
25000040 | Blackout close | Texts related to breaker operations / Parameter name
25000050 | Delay after Hz/V OK before close | Texts related to breaker operations / Parameter name
25000060 | MB close delay | Texts related to breaker operations / Parameter name
25000070 | BTB supply | Texts related to breaker operations / Parameter name
25000160 | Overlap | Texts related to breaker operations / Parameter name
25000170 | Blackout close | Texts related to breaker operations / Parameter name
25000180 | Overlap position failure | Texts related to breaker operations / Alarm text (pop-ups and logs)
25000190 | Blackout close | Texts related to breaker operations / Parameter name
25000200 | Tie breaker normally open/closed | Texts related to breaker operations / Parameter name
25100000 | Emergency busbar status GB side | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
25100001 | Emergency busbar status TB side | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
25100002 | MB virtual busbar status | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
25100003 | Overlap position failure | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
25100004 | TB virtual busbar status | Texts related to breaker operations / Assignable function (input/output config menus, Modbus)
25200000 | Blackout close is OFF | Texts related to breaker operations / Parameter configuration (selected from a list)
25200001 | Generator OK, busbar is dead | Texts related to breaker operations / Parameter configuration (selected from a list)
25200002 | One busbar is alive | Texts related to breaker operations / Parameter configuration (selected from a list)
25200003 | On | Texts related to breaker operations / Parameter configuration (selected from a list)
25200004 | Busbar A is dead, busbar B OK | Texts related to breaker operations / Parameter configuration (selected from a list)
25200005 | Busbar A OK, busbar B is dead | Texts related to breaker operations / Parameter configuration (selected from a list)
25200006 | Shore connection is dead, busbar OK | Texts related to breaker operations / Parameter configuration (selected from a list)
25200007 | Shore connection OK, busbar is dead | Texts related to breaker operations / Parameter configuration (selected from a list)
25200008 | Generator is dead, busbar OK | Texts related to breaker operations / Parameter configuration (selected from a list)
25200009 | Mains is dead, busbar OK | Texts related to breaker operations / Parameter configuration (selected from a list)
25200010 | Mains OK, busbar is dead | Texts related to breaker operations / Parameter configuration (selected from a list)
25200011 | Any busbar voltage/frequency not OK | Texts related to breaker operations / Parameter configuration (selected from a list)
25200012 | Load point is dead, busbar OK | Texts related to breaker operations / Parameter configuration (selected from a list)
25200013 | Load point OK, busbar is dead | Texts related to breaker operations / Parameter configuration (selected from a list)
25200014 | Close GB | Texts related to breaker operations / Parameter configuration (selected from a list)
25200015 | Close GB and TB | Texts related to breaker operations / Parameter configuration (selected from a list)
25200016 | DC voltage | Texts related to breaker operations / Parameter configuration (selected from a list)
25200017 | AC voltage | Texts related to breaker operations / Parameter configuration (selected from a list)
30000000 | Droop | Texts related to synchronisation / Parameter name
30000010 | Droop | Texts related to synchronisation / Parameter name
30000020 | Droop | Texts related to synchronisation / Parameter name
30000030 | Droop | Texts related to synchronisation / Parameter name
30001090 | GB vector mismatch | Texts related to synchronisation / Alarm text (pop-ups and logs)
30010100 | GB vector mismatch | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
30020090 | SGB vector mismatch | Texts related to synchronisation / Alarm text (pop-ups and logs)
30020100 | SGB vector mismatch | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
30030090 | SCB vector mismatch | Texts related to synchronisation / Alarm text (pop-ups and logs)
30030100 | SCB vector mismatch | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
30040090 | BTB vector mismatch | Texts related to synchronisation / Alarm text (pop-ups and logs)
30040100 | BTB vector mismatch | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
30050090 | TB vector mismatch | Texts related to synchronisation / Alarm text (pop-ups and logs)
30050100 | TB vector mismatch | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
30080090 | Breaker vector mismatch | Texts related to synchronisation / Alarm text (pop-ups and logs)
30080100 | Breaker vector mismatch | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
30500000 | Static | Texts related to synchronisation / Parameter configuration (selected from a list)
30500001 | Dynamic | Texts related to synchronisation / Parameter configuration (selected from a list)
30500002 | Automatic | Texts related to synchronisation / Parameter configuration (selected from a list)
30500010 | Delta frequency min. | Texts related to synchronisation / Parameter name
30500011 | Delta frequency max. | Texts related to synchronisation / Parameter name
30500012 | Delta voltage min. | Texts related to synchronisation / Parameter name
30500013 | Delta voltage max. | Texts related to synchronisation / Parameter name
30500014 | Breaker close time | Texts related to synchronisation / Parameter name
30500015 | Phase window | Texts related to synchronisation / Parameter name
30500016 | Minimum time in phase window | Texts related to synchronisation / Parameter name
30500017 | Sync type | Texts related to synchronisation / Parameter name
30500018 | Sync behavior | Texts related to synchronisation / Parameter name
30500030 | Sync check | Texts related to synchronisation / Assignable function (input/output config menus, Modbus)
30500050 | Slip frequency too high | Texts related to synchronisation / Status text (info lines)
30500051 | Slip frequency too low | Texts related to synchronisation / Status text (info lines)
30500052 | Any phase outside sync. window | Texts related to synchronisation / Status text (info lines)
30500053 | Any voltage too high | Texts related to synchronisation / Status text (info lines)
30500054 | Any voltage too low | Texts related to synchronisation / Status text (info lines)
30500055 | Vector mismatch | Texts related to synchronisation / Status text (info lines)
30500056 | Sync. in progress | Texts related to synchronisation / Status text (info lines)
30500057 | Dynamic sync. in progress | Texts related to synchronisation / Status text (info lines)
30500058 | Static sync. in progress | Texts related to synchronisation / Status text (info lines)
30500070 | Generator breaker | Texts related to synchronisation / Miscellaneous text (various uses)
30500071 | Shaft breaker | Texts related to synchronisation / Miscellaneous text (various uses)
30500072 | Bus tie breaker | Texts related to synchronisation / Miscellaneous text (various uses)
30500073 | Shore breaker | Texts related to synchronisation / Miscellaneous text (various uses)
30500074 | Tie breaker | Texts related to synchronisation / Miscellaneous text (various uses)
30500075 | Mains breaker | Texts related to synchronisation / Miscellaneous text (various uses)
30500076 | Inverter breaker | Texts related to synchronisation / Miscellaneous text (various uses)
30600000 | Sync check OK | Texts related to synchronisation / Parameter name
30600100 | GB static synchronisation | Texts related to synchronisation / Parameter name
30600101 | GB dynamic synchronisation | Texts related to synchronisation / Parameter name
30602000 | SGB static synchronisation | Texts related to synchronisation / Parameter name
30602001 | SGB dynamic synchronisation | Texts related to synchronisation / Parameter name
30603000 | SCB static synchronisation | Texts related to synchronisation / Parameter name
30603001 | SCB dynamic synchronisation | Texts related to synchronisation / Parameter name
30604000 | BTB static synchronisation | Texts related to synchronisation / Parameter name
30604001 | BTB dynamic synchronisation | Texts related to synchronisation / Parameter name
30605000 | TB static synchronisation | Texts related to synchronisation / Parameter name
30605001 | TB dynamic synchronisation | Texts related to synchronisation / Parameter name
30606000 | MB static synchronisation | Texts related to synchronisation / Parameter name
30606001 | MB dynamic synchronisation | Texts related to synchronisation / Parameter name
30607000 | Delta frequency above max. | Texts related to synchronisation / Parameter name
30607001 | Delta frequency below min. | Texts related to synchronisation / Parameter name
30607002 | Delta voltage above max. | Texts related to synchronisation / Parameter name
30607003 | Delta voltage below min. | Texts related to synchronisation / Parameter name
30607004 | Vector mismatch | Texts related to synchronisation / Parameter name
30607005 | Phase angle outside window | Texts related to synchronisation / Parameter name
30607006 | Sync. status | Texts related to synchronisation / Parameter name
30607007 | Inside window | Texts related to synchronisation / Parameter name
30607008 | Synchronisation in progress | Texts related to synchronisation / Parameter name
30607050 | Delta frequency above max. | Texts related to synchronisation / Parameter name
30607051 | Delta frequency below min. | Texts related to synchronisation / Parameter name
30607052 | Delta voltage above max. | Texts related to synchronisation / Parameter name
30607053 | Delta voltage below min. | Texts related to synchronisation / Parameter name
30607054 | Vector mismatch | Texts related to synchronisation / Parameter name
30607055 | Phase angle outside window | Texts related to synchronisation / Parameter name
30607056 | Sync. status | Texts related to synchronisation / Parameter name
30607057 | Inside window | Texts related to synchronisation / Parameter name
30607058 | Synchronisation in progress | Texts related to synchronisation / Parameter name
30608000 | Breaker static synchronisation | Texts related to synchronisation / Parameter name
30608001 | Breaker dynamic synchronisation | Texts related to synchronisation / Parameter name
31000000 | GENSET controller | Text related to controller variant / Label text
31000001 | EMERGENCY genset controller | Text related to controller variant / Label text
31000002 | SHAFT generator controller | Text related to controller variant / Label text
31000003 | SHORE connection controller | Text related to controller variant / Label text
31000004 | BUS TIE breaker controller | Text related to controller variant / Label text
31000005 | MAINS controller | Text related to controller variant / Label text
31000006 | Mains - No breaker | Text related to controller variant / Label text
31000007 | Mains - Standard | Text related to controller variant / Label text
31000008 | Mains - Load busbar | Text related to controller variant / Label text
31000009 | Single genset - With mains breaker | Text related to controller variant / Label text
31000010 | Single genset - No mains breaker | Text related to controller variant / Label text
31000011 | I/O controller | Text related to controller variant / Label text
31000012 | HYBRID controller | Text related to controller variant / Label text
31000013 | Single genset - No mains | Text related to controller variant / Label text
31001000 | Standard unit | Text related to controller variant / Label text
31001010 | Mains unit | Text related to controller variant / Label text
31001020 | BTB unit | Text related to controller variant / Label text
32000000 | Relay type | Texts related to the ground relay feature / Parameter name
32000010 | Close configuration | Texts related to the ground relay feature / Parameter name
32000020 | Open configuration | Texts related to the ground relay feature / Parameter name
32000030 | Ground relay general failure | Texts related to the ground relay feature / Alarm text (pop-ups and logs)
32000040 | Ground relay | Texts related to the ground relay feature / Parameter name
32000050 | RPM level | Texts related to the ground relay feature / Parameter name
32000060 | Ground relay open failure | Texts related to the ground relay feature / Alarm text (pop-ups and logs)
32000070 | Ground relay close failure | Texts related to the ground relay feature / Alarm text (pop-ups and logs)
32000080 | Ground relay position failure | Texts related to the ground relay feature / Alarm text (pop-ups and logs)
32100000 | Continuous | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100001 | Pulse | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100002 | Hz/V OK | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100003 | RPM MPU level | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100004 | RPM EIC level | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100005 | Start active | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100006 | After cooldown | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100007 | After extended stop | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100008 | Ground relay | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100009 | Ground relay configuration | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100010 | Ground relay general failure | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100011 | Enable | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100012 | Ground relay open failure | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100013 | Ground relay close failure | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32100014 | Ground relay position failure | Texts related to the ground relay feature / Menu text (menu hierachy and labels)
32200000 | Ground relay A | Texts related to the ground relay feature / Assignable function (input/output config menus, Modbus)
32200001 | Ground relay B | Texts related to the ground relay feature / Assignable function (input/output config menus, Modbus)
32200002 | Ground relay position feedback A | Texts related to the ground relay feature / Assignable function (input/output config menus, Modbus)
32200003 | Ground relay position feedback B | Texts related to the ground relay feature / Assignable function (input/output config menus, Modbus)
32200004 | Ground relay failure | Texts related to the ground relay feature / Assignable function (input/output config menus, Modbus)
32200005 | Ground relay open failure | Texts related to the ground relay feature / Assignable function (input/output config menus, Modbus)
32200006 | Ground relay close failure | Texts related to the ground relay feature / Assignable function (input/output config menus, Modbus)
32200007 | Ground relay position failure | Texts related to the ground relay feature / Assignable function (input/output config menus, Modbus)
32300000 | Ground breaker on | Texts related to the ground relay feature / Event text (pop-ups, logs and status texts)
32300010 | Ground breaker off | Texts related to the ground relay feature / Event text (pop-ups, logs and status texts)
33000000 | Breaker close set point | Texts related to the CBE feature / Parameter name
33000010 | Timer crank release to AVR on | Texts related to the CBE feature / Alarm text (pop-ups and logs)
33000050 | CBE rerun failure | Texts related to the CBE feature / Alarm text (pop-ups and logs)
33000060 | Breakers to close | Texts related to the CBE feature / Parameter name
33000070 | Soft-start timer | Texts related to the CBE feature / Parameter name
33000080 | Minimum RPM for excitation | Texts related to the CBE feature / Parameter name
33000090 | Voltage discharge timer for GB close | Texts related to the CBE feature / Parameter name
33000100 | Maximum rerun voltage for GB close | Texts related to the CBE feature / Parameter name
33000110 | Excitation control during cooldown | Texts related to the CBE feature / Parameter name
33000120 | Close before excitation failure | Texts related to the CBE feature / Alarm text (pop-ups and logs)
33010005 | Close before excitation configuration error | Texts related to the CBE feature / Menu text (menu hierachy and labels)
33010006 | Close before excitation voltage discharge in | Texts related to the CBE feature / Menu text (menu hierachy and labels)
33010007 | Close before excitation await low voltage | Texts related to the CBE feature / Menu text (menu hierachy and labels)
33010008 | Excitation follow U busbar | Texts related to the CBE feature / Menu text (menu hierachy and labels)
33010009 | Excitation constant ON | Texts related to the CBE feature / Menu text (menu hierachy and labels)
33010010 | Excitation OFF | Texts related to the CBE feature / Menu text (menu hierachy and labels)
33020000 | CBE AVR relay | Texts related to the CBE feature / Assignable function (input/output config menus, Modbus)
33020001 | Synchronisation failure | Texts related to the CBE feature / Assignable function (input/output config menus, Modbus)
33020002 | Sync rerun fail | Texts related to the CBE feature / Assignable function (input/output config menus, Modbus)
39100000 | Winding nominal voltage source | Texts related to AC measurements and calculations / Parameter name
39100001 | Phase shift | Texts related to AC measurements and calculations / Parameter name
39100010 | Busbar side winding nominal voltage | Texts related to AC measurements and calculations / Parameter name
39100011 | Mains side winding nominal voltage | Texts related to AC measurements and calculations / Parameter name
39100012 | Busbar side winding nominal voltage | Texts related to AC measurements and calculations / Parameter name
39100020 | Generator side winding nominal voltage | Texts related to AC measurements and calculations / Parameter name
39100021 | Inverter side winding nominal voltage | Texts related to AC measurements and calculations / Parameter name
39100022 | Generator side winding nominal voltage | Texts related to AC measurements and calculations / Parameter name
39100023 | Generator side winding nominal voltage | Texts related to AC measurements and calculations / Parameter name
40000900 | Nominal settings 1 | Texts related to AC measurements and calculations / Label text
40000901 | Nominal settings 2 | Texts related to AC measurements and calculations / Label text
40000902 | Nominal settings 3 | Texts related to AC measurements and calculations / Label text
40000903 | Nominal settings 4 | Texts related to AC measurements and calculations / Label text
40000904 | Q nominal calculated | Texts related to AC measurements and calculations / Label text
40000905 | Q nominal = P nominal | Texts related to AC measurements and calculations / Label text
40000906 | Q nominal = S nominal | Texts related to AC measurements and calculations / Label text
40000907 | No calculation | Texts related to AC measurements and calculations / Label text
40000908 | P nominal calculated | Texts related to AC measurements and calculations / Label text
40000909 | S nominal calculated | Texts related to AC measurements and calculations / Label text
40000910 | Selection | Texts related to AC measurements and calculations / Label text
40000911 | Changed nominal settings to set 1 | Texts related to AC measurements and calculations / Label text
40000912 | Changed nominal settings to set 2 | Texts related to AC measurements and calculations / Label text
40000913 | Changed nominal settings to set 3 | Texts related to AC measurements and calculations / Label text
40000914 | Changed nominal settings to set 4 | Texts related to AC measurements and calculations / Label text
40000915 | Nominal settings 1 selected | Texts related to AC measurements and calculations / Label text
40000916 | Nominal settings 2 selected | Texts related to AC measurements and calculations / Label text
40000917 | Nominal settings 3 selected | Texts related to AC measurements and calculations / Label text
40000918 | Nominal settings 4 selected | Texts related to AC measurements and calculations / Label text
40000919 | Nominal setting selected | Texts related to AC measurements and calculations / Label text
40000920 | Use generator nominal voltage | Texts related to AC measurements and calculations / Label text
40000921 | Use busbar A nominal voltage | Texts related to AC measurements and calculations / Label text
40000922 | Use shore busbar nominal voltage | Texts related to AC measurements and calculations / Label text
40000923 | Use reference A nominal voltage | Texts related to AC measurements and calculations / Label text
40000924 | Use mains nominal voltage | Texts related to AC measurements and calculations / Label text
40000925 | User defined | Texts related to AC measurements and calculations / Label text
40000926 | Source | Texts related to AC measurements and calculations / Label text
40000927 | Local | Texts related to AC measurements and calculations / Label text
40000928 | Power management rules | Texts related to AC measurements and calculations / Label text
40000929 | Use nominal voltages | Texts related to AC measurements and calculations / Label text
40005000 | Nominal | Texts related to AC measurements and calculations / Label text
40005001 | Nominal | Texts related to AC measurements and calculations / Label text
40005002 | Nominal | Texts related to AC measurements and calculations / Label text
40005003 | Nominal | Texts related to AC measurements and calculations / Label text
40005004 | Nominal | Texts related to AC measurements and calculations / Label text
40005005 | Nominal (calculated) | Texts related to AC measurements and calculations / Label text
40005006 | Nominal (calculated) | Texts related to AC measurements and calculations / Label text
40005007 | Nominal (calculated) | Texts related to AC measurements and calculations / Label text
40005008 | Nominal | Texts related to AC measurements and calculations / Label text
40005009 | Reactive power (Q) nominal | Texts related to AC measurements and calculations / Label text
40005010 | P or S nominal | Texts related to AC measurements and calculations / Label text
40005011 | Transformer compensation | Texts related to AC measurements and calculations / Label text
40005012 | Nominal | Texts related to AC measurements and calculations / Label text
40005015 | Nominal value source | Texts related to AC measurements and calculations / Label text
40005016 | GOV output offset 1 | Texts related to AC measurements and calculations / Label text
40005017 | AVR output offset 1 | Texts related to AC measurements and calculations / Label text
40005018 | GOV output offset 2 | Texts related to AC measurements and calculations / Label text
40005019 | AVR output offset 2 | Texts related to AC measurements and calculations / Label text
40005020 | GOV output offset 3 | Texts related to AC measurements and calculations / Label text
40005021 | AVR output offset 3 | Texts related to AC measurements and calculations / Label text
40005022 | GOV output offset 4 | Texts related to AC measurements and calculations / Label text
40005023 | AVR output offset 4 | Texts related to AC measurements and calculations / Label text
40130000 | L4 | Texts related to AC measurements and calculations / Used in view designs
40130001 | L4 | Texts related to AC measurements and calculations / Used in view designs
40130002 | L4 | Texts related to AC measurements and calculations / Used in view designs
40130003 | L4 | Texts related to AC measurements and calculations / Used in view designs
40130004 | L4 | Texts related to AC measurements and calculations / Used in view designs
40130005 | P L4 percent | Texts related to AC measurements and calculations / Used in view designs
40130006 | Q L4 percent | Texts related to AC measurements and calculations / Used in view designs
40130007 | S L4 percent | Texts related to AC measurements and calculations / Used in view designs
40130008 | L4 | Texts related to AC measurements and calculations / Used in view designs
40130009 | L4 ¦ cos phi | Texts related to AC measurements and calculations / Used in view designs
40130010 | L4 ¦ Power factor | Texts related to AC measurements and calculations / Used in view designs
40140000 | P total | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40140001 | Q total | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40140002 | S total | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40150000 | ACM3.2 - I L1 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40150001 | ACM3.2 - I L2 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40150002 | ACM3.2 - I L3 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40150003 | ACM3.2 - I min. (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40150004 | ACM3.2 - I max. (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40150025 | ACM3.2 - I L1 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40150026 | ACM3.2 - I L2 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40150027 | ACM3.2 - I L3 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40150028 | ACM3.2 - I min. (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40150029 | ACM3.2 - I max. (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40150050 | ACM3.2 - I L1 diff. | Texts related to AC measurements and calculations / Used in view designs
40150051 | ACM3.2 - I L2 diff. | Texts related to AC measurements and calculations / Used in view designs
40150052 | ACM3.2 - I L3 diff. | Texts related to AC measurements and calculations / Used in view designs
40150053 | ACM3.2 - I min. diff. | Texts related to AC measurements and calculations / Used in view designs
40150054 | ACM3.2 - I max. diff. | Texts related to AC measurements and calculations / Used in view designs
40150055 | ACM3.2 - I L1 restraint | Texts related to AC measurements and calculations / Used in view designs
40150056 | ACM3.2 - I L2 restraint | Texts related to AC measurements and calculations / Used in view designs
40150057 | ACM3.2 - I L3 restraint | Texts related to AC measurements and calculations / Used in view designs
40150058 | ACM3.2 - I min. restraint | Texts related to AC measurements and calculations / Used in view designs
40150059 | ACM3.2 - I max. restraint | Texts related to AC measurements and calculations / Used in view designs
40150060 | ACM3.2 - I frequency | Texts related to AC measurements and calculations / Used in view designs
40210000 | Active energy export | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40210100 | Reactive energy export | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40210200 | Active energy import | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40210300 | Reactive energy import | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40210400 | Active energy difference | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40210500 | Reactive energy difference | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40211000 | Active energy export 2 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40211100 | Reactive energy export 2 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40211200 | Active energy import 2 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40211300 | Reactive energy import 2 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40211400 | Active energy difference 2 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40211500 | Reactive energy difference 2 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40212000 | Active energy export 3 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40212100 | Reactive energy export 3 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40212200 | Active energy import 3 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40212300 | Reactive energy import 3 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40212310 | Pulse every 3 | Texts related to AC measurements and calculations / Parameter name
40212320 | Pulse length 3 | Texts related to AC measurements and calculations / Timer text
40212400 | Active energy difference 3 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40212500 | Reactive energy difference 3 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40213000 | Active energy export 4 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40213100 | Reactive energy export 4 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40213200 | Active energy import 4 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40213300 | Reactive energy import 4 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40213400 | Active energy difference 4 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40213500 | Reactive energy difference 4 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40214000 | Active energy export 5 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40214100 | Reactive energy export 5 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40214200 | Active energy import 5 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40214300 | Reactive energy import 5 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40214400 | Active energy difference 5 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40214500 | Reactive energy difference 5 | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240000 | Pulse every | Texts related to AC measurements and calculations / Parameter name
40240001 | Pulse length | Texts related to AC measurements and calculations / Timer text
40240010 | Active energy export pulse | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240011 | Reactive energy export pulse | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240012 | Active energy import pulse | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240013 | Reactive energy import pulse | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240014 | Active energy difference pulse | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240015 | Reactive energy difference pulse | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240100 | Active energy export (transducer %s) | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240101 | Reactive energy export (transducer %s) | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240102 | Active energy import (transducer %s) | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240103 | Reactive energy import (transducer %s) | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240104 | Active energy difference (transducer %s) | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40240105 | Reactive energy difference (transducer %s) | Texts related to AC measurements and calculations / An assignable function (CustomLogic)
40340000 | 1 | Texts related to AC measurements and calculations / Parameter name
40340001 | 5 | Texts related to AC measurements and calculations / Parameter name
40340010 | Primary | Texts related to AC measurements and calculations / Parameter name
40340011 | Secondary | Texts related to AC measurements and calculations / Parameter name
40340012 | Primary (I4) | Texts related to AC measurements and calculations / Parameter name
40340013 | Secondary (I4) | Texts related to AC measurements and calculations / Parameter name
40350000 | Primary | Texts related to AC measurements and calculations / Parameter name
40350010 | Secondary | Texts related to AC measurements and calculations / Parameter name
40350020 | Primary | Texts related to AC measurements and calculations / Parameter name
40350030 | Secondary | Texts related to AC measurements and calculations / Parameter name
40360000 | Current reference dir. | Texts related to AC measurements and calculations / Parameter name
40360010 | Current reference dir. | Texts related to AC measurements and calculations / Parameter name
40370000 | Towards prot. obj. | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40370010 | Away from prot. obj. | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40407000 | Blackout on busbar | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40407010 | Busbar voltage and frequency OK | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40407020 | Blackout on busbar A | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40407030 | Busbar A voltage and frequency OK | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40407040 | Blackout on mains | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40407050 | Mains voltage and frequency OK | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40410170 | Low voltage hysteresis | Texts related to AC measurements and calculations / Parameter name
40410180 | High voltage hysteresis | Texts related to AC measurements and calculations / Parameter name
40410190 | Low frequency hysteresis | Texts related to AC measurements and calculations / Parameter name
40410200 | High frequency hysteresis | Texts related to AC measurements and calculations / Parameter name
40410210 | Voltage failure delay | Texts related to AC measurements and calculations / Parameter name
40410220 | Voltage OK delay | Texts related to AC measurements and calculations / Parameter name
40410230 | Low voltage | Texts related to AC measurements and calculations / Parameter name
40410250 | High voltage | Texts related to AC measurements and calculations / Parameter name
40410260 | Voltage failure sequence | Texts related to AC measurements and calculations / Parameter name
40410270 | Unbalance voltage | Texts related to AC measurements and calculations / Parameter name
40410280 | Frequency failure delay | Texts related to AC measurements and calculations / Parameter name
40410290 | Frequency OK delay | Texts related to AC measurements and calculations / Parameter name
40410300 | Low frequency | Texts related to AC measurements and calculations / Parameter name
40410310 | High frequency | Texts related to AC measurements and calculations / Parameter name
40416000 | Frequency too low | Texts related to AC measurements and calculations / Status text (info lines)
40416001 | Frequency too high | Texts related to AC measurements and calculations / Status text (info lines)
40416002 | Voltage too low | Texts related to AC measurements and calculations / Status text (info lines)
40416003 | Voltage too high | Texts related to AC measurements and calculations / Status text (info lines)
40417000 | Blackout on shore busbar | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40417010 | Shore connection voltage and frequency OK | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40417020 | Blackout on busbar B | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40417030 | Busbar B voltage and frequency OK | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40417040 | Blackout on mains | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40417050 | Mains voltage and frequency OK | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40417060 | Shaft generator voltage and frequency dead | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40417070 | Shaft generator voltage and frequency OK | Texts related to AC measurements and calculations / Event text (pop-ups, logs and status texts)
40499000 | Voltage and frequency OK | Texts related to AC measurements and calculations / Timer text
40499001 | Minimum OK voltage | Texts related to AC measurements and calculations / Parameter name
40499002 | Maximum OK voltage | Texts related to AC measurements and calculations / Parameter name
40499003 | Minimum OK frequency | Texts related to AC measurements and calculations / Parameter name
40499004 | Maximum OK frequency | Texts related to AC measurements and calculations / Parameter name
40499005 | Maximum voltage balance deviation | Texts related to AC measurements and calculations / Parameter name
40499006 | Maximum phase deviation | Texts related to AC measurements and calculations / Parameter name
40499007 | Detection voltage | Texts related to AC measurements and calculations / Parameter name
40499009 | Phase sequence error | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40499010 | Voltage or frequency not OK | Texts related to AC measurements and calculations / Alarm text (pop-ups and logs)
40499011 | Blackout delay | Texts related to AC measurements and calculations / Timer text
40499050 | Voltage or frequency not OK | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40499051 | State | Texts related to AC measurements and calculations / Parameter name
40499052 | Voltage and frequency OK | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40499053 | No voltage and frequency | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40499054 | V/Hz OK in | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40510030 | Source | Texts related to AC measurements and calculations / Parameter name
40550000 | Three-phase | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550001 | Split-phase L1-L3 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550002 | Split-phase L1-L2 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550003 | Single-phase L1 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550004 | L1-L2-L3 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550005 | L1-L3-L2 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550006 | Phase-phase | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550007 | Phase-neutral | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550008 | Three-phase (2 CT, L1-L3) | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550009 | Split-phase L2-L3 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550010 | Single-phase L2 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550011 | Single-phase L3 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40550012 | Phase-phase or phase-neutral | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40551000 | None | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40551001 | I4 | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40551002 | Analogue input | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40551100 | AC configuration | Texts related to AC measurements and calculations / Parameter name
40551101 | AC phase rotation | Texts related to AC measurements and calculations / Parameter name
40551102 | AC setup | Texts related to AC measurements and calculations / Parameter name
40600000 | Derate curve | Texts related to AC measurements and calculations / Graph text (heading or axis name)
40600500 | Enable derate | Texts related to AC measurements and calculations / Parameter name
40600510 | Derate 1 temperature | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40601000 | Derate curve | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40601500 | Enable derate | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40610000 | Derate curve | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40610500 | Enable derate | Texts related to AC measurements and calculations / Parameter name
40610510 | Derate 2 temperature | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40620000 | Derate curve | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40620500 | Enable derate | Texts related to AC measurements and calculations / Parameter name
40620510 | Derate 3 temperature | Texts related to AC measurements and calculations / Assignable function (input/output config menus, Modbus)
40630000 | Temperature | Texts related to AC measurements and calculations / Graph text (heading or axis name)
40630001 | Power rating | Texts related to AC measurements and calculations / Graph text (heading or axis name)
40630002 | Derated to | Texts related to AC measurements and calculations / Graph text (heading or axis name)
40630100 | RPM | Texts related to AC measurements and calculations / Graph text (heading or axis name)
40630101 | RPM power rating | Texts related to AC measurements and calculations / Graph text (heading or axis name)
40640000 | Enable derate | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40640010 | Derate percentage | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40650000 | Derate curve | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40650500 | Enable derate | Texts related to AC measurements and calculations / Miscellaneous text (various uses)
40700000 | Generator ¦ L1-N | Texts related to AC measurements and calculations / Used in view designs
40700001 | Generator ¦ L2-N | Texts related to AC measurements and calculations / Used in view designs
40700002 | Generator ¦ L3-N | Texts related to AC measurements and calculations / Used in view designs
40700003 | Generator ¦ N | Texts related to AC measurements and calculations / Used in view designs
40700004 | Generator ¦ L-N min. | Texts related to AC measurements and calculations / Used in view designs
40700005 | Generator ¦ L-N max. | Texts related to AC measurements and calculations / Used in view designs
40700006 | Generator ¦ L-N unbalanced | Texts related to AC measurements and calculations / Used in view designs
40700007 | Generator ¦ L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40700008 | Generator ¦ L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40700009 | Generator ¦ L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40700010 | Generator ¦ L-L min. | Texts related to AC measurements and calculations / Used in view designs
40700011 | Generator ¦ L-L max. | Texts related to AC measurements and calculations / Used in view designs
40700012 | Generator ¦ L-L unbalanced | Texts related to AC measurements and calculations / Used in view designs
40700013 | Generator ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40700014 | Generator ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40700015 | Generator ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40700016 | Generator ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40700017 | Generator ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40700018 | Generator ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40700019 | Generator ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40700020 | Generator ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40700021 | Generator ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40700022 | Generator ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40700023 | Generator ¦ A-B phase angle L1 | Texts related to AC measurements and calculations / Used in view designs
40700024 | Generator ¦ A-B phase angle L2 | Texts related to AC measurements and calculations / Used in view designs
40700025 | Generator ¦ A-B phase angle L3 | Texts related to AC measurements and calculations / Used in view designs
40700026 | Generator ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40700027 | Generator ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40700028 | Generator ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40700029 | Generator ¦ N | Texts related to AC measurements and calculations / Used in view designs
40700030 | Generator ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40700031 | Generator ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40700032 | Generator ¦ Unbalanced nominal | Texts related to AC measurements and calculations / Used in view designs
40700033 | Generator ¦ Unbalanced average | Texts related to AC measurements and calculations / Used in view designs
40700034 | Generator ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40700035 | Generator ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40700036 | Generator ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40700037 | Generator ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40700038 | Generator ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40700039 | Generator ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40700040 | Generator ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40700041 | Generator ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40700042 | Generator ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40700043 | Generator ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40700044 | Generator ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40700045 | Generator ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40700046 | Generator ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40700047 | Generator ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40700048 | Generator ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40700049 | Generator ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40700050 | Generator ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40700051 | Generator ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40700052 | Generator ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40700053 | Generator ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40700054 | Generator ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40700055 | Generator ¦ cos phi | Texts related to AC measurements and calculations / Used in view designs
40700056 | Generator ¦ Power factor | Texts related to AC measurements and calculations / Used in view designs
40700057 | Generator ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40700058 | Generator ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40700059 | Generator ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40700060 | Generator ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40700061 | Generator ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40700062 | Generator ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40700063 | Generator ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40700064 | Generator ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40700065 | Generator ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40700066 | Generator ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40700067 | Generator ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40700068 | Generator ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40700069 | Generator ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40700070 | Generator ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40700071 | Generator ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40700072 | Generator ¦ State | Texts related to AC measurements and calculations / Used in view designs
40700100 | Generator ¦ L1 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40700101 | Generator ¦ L2 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40700102 | Generator ¦ L3 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40700103 | Generator ¦ Min. (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40700104 | Generator ¦ Max. (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40700110 | Generator ¦ L1 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40700111 | Generator ¦ L2 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40700112 | Generator ¦ L3 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40700113 | Generator ¦ Min. (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40700114 | Generator ¦ Max. (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40700120 | Generator ¦ L1 differential | Texts related to AC measurements and calculations / Used in view designs
40700121 | Generator ¦ L2 differential | Texts related to AC measurements and calculations / Used in view designs
40700122 | Generator ¦ L3 differential | Texts related to AC measurements and calculations / Used in view designs
40700123 | Generator ¦ Min. differential | Texts related to AC measurements and calculations / Used in view designs
40700124 | Generator ¦ Max. differential | Texts related to AC measurements and calculations / Used in view designs
40700130 | Generator ¦ L1 restraint | Texts related to AC measurements and calculations / Used in view designs
40700131 | Generator ¦ L2 restraint | Texts related to AC measurements and calculations / Used in view designs
40700132 | Generator ¦ L3 restraint | Texts related to AC measurements and calculations / Used in view designs
40700133 | Generator ¦ Min. restraint | Texts related to AC measurements and calculations / Used in view designs
40700134 | Generator ¦ Max. restraint | Texts related to AC measurements and calculations / Used in view designs
40700140 | Generator ¦ Frequency | Texts related to AC measurements and calculations / Used in view designs
40710000 | Busbar ¦ L1-N | Texts related to AC measurements and calculations / Used in view designs
40710001 | Busbar ¦ L2-N | Texts related to AC measurements and calculations / Used in view designs
40710002 | Busbar ¦ L3-N | Texts related to AC measurements and calculations / Used in view designs
40710003 | Busbar ¦ N | Texts related to AC measurements and calculations / Used in view designs
40710004 | Busbar ¦ L-N min. | Texts related to AC measurements and calculations / Used in view designs
40710005 | Busbar ¦ L-N max. | Texts related to AC measurements and calculations / Used in view designs
40710006 | Busbar ¦ L-N unbalanced | Texts related to AC measurements and calculations / Used in view designs
40710007 | Busbar ¦ L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40710008 | Busbar ¦ L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40710009 | Busbar ¦ L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40710010 | Busbar ¦ L-L min. | Texts related to AC measurements and calculations / Used in view designs
40710011 | Busbar ¦ L-L max. | Texts related to AC measurements and calculations / Used in view designs
40710012 | Busbar ¦ L-L unbalanced | Texts related to AC measurements and calculations / Used in view designs
40710013 | Busbar ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40710014 | Busbar ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40710015 | Busbar ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40710016 | Busbar ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40710017 | Busbar ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40710018 | Busbar ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40710019 | Busbar ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40710020 | Busbar ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40710021 | Busbar ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40710022 | Busbar ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40710023 | Busbar ¦ Phase angle L1 | Texts related to AC measurements and calculations / Used in view designs
40710024 | Busbar ¦ Phase angle L2 | Texts related to AC measurements and calculations / Used in view designs
40710025 | Busbar ¦ Phase angle L3 | Texts related to AC measurements and calculations / Used in view designs
40710026 | Busbar ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40710027 | Busbar ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40710028 | Busbar ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40710029 | Busbar ¦ N | Texts related to AC measurements and calculations / Used in view designs
40710030 | Busbar ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40710031 | Busbar ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40710032 | Busbar ¦ Unbalanced nominal | Texts related to AC measurements and calculations / Used in view designs
40710033 | Busbar ¦ Unbalanced average | Texts related to AC measurements and calculations / Used in view designs
40710034 | Busbar ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40710035 | Busbar ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40710036 | Busbar ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40710037 | Busbar ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40710038 | Busbar ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40710039 | Busbar ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40710040 | Busbar ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40710041 | Busbar ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40710042 | Busbar ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40710043 | Busbar ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40710044 | Busbar ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40710045 | Busbar ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40710046 | Busbar ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40710047 | Busbar ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40710048 | Busbar ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40710049 | Busbar ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40710050 | Busbar ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40710051 | Busbar ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40710052 | Busbar ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40710053 | Busbar ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40710054 | Busbar ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40710055 | Busbar ¦ cos phi | Texts related to AC measurements and calculations / Used in view designs
40710056 | Busbar ¦ Power factor | Texts related to AC measurements and calculations / Used in view designs
40710057 | Busbar ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40710058 | Busbar ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40710059 | Busbar ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40710060 | Busbar ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40710061 | Busbar ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40710062 | Busbar ¦ State | Texts related to AC measurements and calculations / Used in view designs
40710063 | Busbar ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40710064 | Busbar ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40710065 | Busbar ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40710066 | Busbar ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40710067 | Busbar ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40710068 | Busbar ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40710069 | Busbar ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40710070 | Busbar ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40710071 | Busbar ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40710072 | Busbar ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40720000 | Busbar A ¦ L1-N | Texts related to AC measurements and calculations / Used in view designs
40720001 | Busbar A ¦ L2-N | Texts related to AC measurements and calculations / Used in view designs
40720002 | Busbar A ¦ L3-N | Texts related to AC measurements and calculations / Used in view designs
40720003 | Busbar A ¦ N | Texts related to AC measurements and calculations / Used in view designs
40720004 | Busbar A ¦ L-N min. | Texts related to AC measurements and calculations / Used in view designs
40720005 | Busbar A ¦ L-N max. | Texts related to AC measurements and calculations / Used in view designs
40720006 | Busbar A ¦ L-N unbalanced | Texts related to AC measurements and calculations / Used in view designs
40720007 | Busbar A ¦ L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40720008 | Busbar A ¦ L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40720009 | Busbar A ¦ L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40720010 | Busbar A ¦ L-L min. | Texts related to AC measurements and calculations / Used in view designs
40720011 | Busbar A ¦ L-L max. | Texts related to AC measurements and calculations / Used in view designs
40720012 | Busbar A ¦ L-L unbalanced | Texts related to AC measurements and calculations / Used in view designs
40720013 | Busbar A ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40720014 | Busbar A ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40720015 | Busbar A ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40720016 | Busbar A ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40720017 | Busbar A ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40720018 | Busbar A ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40720019 | Busbar A ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40720020 | Busbar A ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40720021 | Busbar A ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40720022 | Busbar A ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40720023 | Busbar A ¦ Phase angle L1 | Texts related to AC measurements and calculations / Used in view designs
40720024 | Busbar A ¦ Phase angle L2 | Texts related to AC measurements and calculations / Used in view designs
40720025 | Busbar A ¦ Phase angle L3 | Texts related to AC measurements and calculations / Used in view designs
40720026 | Busbar A ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40720027 | Busbar A ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40720028 | Busbar A ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40720029 | Busbar A ¦ N | Texts related to AC measurements and calculations / Used in view designs
40720030 | Busbar A ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40720031 | Busbar A ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40720032 | Busbar A ¦ Unbalanced nominal | Texts related to AC measurements and calculations / Used in view designs
40720033 | Busbar A ¦ Unbalanced average | Texts related to AC measurements and calculations / Used in view designs
40720034 | Busbar A ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40720035 | Busbar A ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40720036 | Busbar A ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40720037 | Busbar A ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40720038 | Busbar A ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40720039 | Busbar A ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40720040 | Busbar A ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40720041 | Busbar A ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40720042 | Busbar A ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40720043 | Busbar A ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40720044 | Busbar A ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40720045 | Busbar A ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40720046 | Busbar A ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40720047 | Busbar A ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40720048 | Busbar A ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40720049 | Busbar A ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40720050 | Busbar A ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40720051 | Busbar A ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40720052 | Busbar A ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40720053 | Busbar A ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40720054 | Busbar A ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40720055 | Busbar A ¦ cos phi | Texts related to AC measurements and calculations / Used in view designs
40720056 | Busbar A ¦ Power factor | Texts related to AC measurements and calculations / Used in view designs
40720057 | Busbar A ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40720058 | Busbar A ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40720059 | Busbar A ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40720060 | Busbar A ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40720061 | Busbar A ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40720062 | Busbar A ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40720063 | Busbar A ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40720064 | Busbar A ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40720065 | Busbar A ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40720066 | Busbar A ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40720067 | Busbar A ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40720068 | Busbar A ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40720069 | Busbar A ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40720070 | Busbar A ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40720071 | Busbar A ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40720072 | Busbar A ¦ State | Texts related to AC measurements and calculations / Used in view designs
40730000 | Busbar B ¦ L1-N | Texts related to AC measurements and calculations / Used in view designs
40730001 | Busbar B ¦ L2-N | Texts related to AC measurements and calculations / Used in view designs
40730002 | Busbar B ¦ L3-N | Texts related to AC measurements and calculations / Used in view designs
40730003 | Busbar B ¦ N | Texts related to AC measurements and calculations / Used in view designs
40730004 | Busbar B ¦ L-N min. | Texts related to AC measurements and calculations / Used in view designs
40730005 | Busbar B ¦ L-N max. | Texts related to AC measurements and calculations / Used in view designs
40730006 | Busbar B ¦ L-N unbalanced | Texts related to AC measurements and calculations / Used in view designs
40730007 | Busbar B ¦ L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40730008 | Busbar B ¦ L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40730009 | Busbar B ¦ L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40730010 | Busbar B ¦ L-L min. | Texts related to AC measurements and calculations / Used in view designs
40730011 | Busbar B ¦ L-L max. | Texts related to AC measurements and calculations / Used in view designs
40730012 | Busbar B ¦ L-L unbalanced | Texts related to AC measurements and calculations / Used in view designs
40730013 | Busbar B ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40730014 | Busbar B ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40730015 | Busbar B ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40730016 | Busbar B ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40730017 | Busbar B ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40730018 | Busbar B ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40730019 | Busbar B ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40730020 | Busbar B ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40730021 | Busbar B ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40730022 | Busbar B ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40730023 | Busbar B ¦ Phase angle L1 | Texts related to AC measurements and calculations / Used in view designs
40730024 | Busbar B ¦ Phase angle L2 | Texts related to AC measurements and calculations / Used in view designs
40730025 | Busbar B ¦ Phase angle L3 | Texts related to AC measurements and calculations / Used in view designs
40730026 | Busbar B ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40730027 | Busbar B ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40730028 | Busbar B ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40730029 | Busbar B ¦ N | Texts related to AC measurements and calculations / Used in view designs
40730030 | Busbar B ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40730031 | Busbar B ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40730032 | Busbar B ¦ Unbalanced nominal | Texts related to AC measurements and calculations / Used in view designs
40730033 | Busbar B ¦ Unbalanced average | Texts related to AC measurements and calculations / Used in view designs
40730034 | Busbar B ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40730035 | Busbar B ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40730036 | Busbar B ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40730037 | Busbar B ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40730038 | Busbar B ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40730039 | Busbar B ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40730040 | Busbar B ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40730041 | Busbar B ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40730042 | Busbar B ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40730043 | Busbar B ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40730044 | Busbar B ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40730045 | Busbar B ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40730046 | Busbar B ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40730047 | Busbar B ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40730048 | Busbar B ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40730049 | Busbar B ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40730050 | Busbar B ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40730051 | Busbar B ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40730052 | Busbar B ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40730053 | Busbar B ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40730054 | Busbar B ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40730055 | Busbar B ¦ cos phi | Texts related to AC measurements and calculations / Used in view designs
40730056 | Busbar B ¦ Power factor | Texts related to AC measurements and calculations / Used in view designs
40730057 | Busbar B ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40730058 | Busbar B ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40730059 | Busbar B ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40730060 | Busbar B ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40730061 | Busbar B ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40730062 | Busbar B ¦ State | Texts related to AC measurements and calculations / Used in view designs
40730063 | Busbar B ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40730064 | Busbar B ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40730065 | Busbar B ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40730066 | Busbar B ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40730067 | Busbar B ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40730068 | Busbar B ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40730069 | Busbar B ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40730070 | Busbar B ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40730071 | Busbar B ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40730072 | Busbar B ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40750000 | Shore ¦ L1-N | Texts related to AC measurements and calculations / Status text (info lines)
40750001 | Shore ¦ L2-N | Texts related to AC measurements and calculations / Status text (info lines)
40750002 | Shore ¦ L3-N | Texts related to AC measurements and calculations / Status text (info lines)
40750003 | Shore ¦ N | Texts related to AC measurements and calculations / Status text (info lines)
40750004 | Shore ¦ L-N min. | Texts related to AC measurements and calculations / Status text (info lines)
40750005 | Shore ¦ L-N max. | Texts related to AC measurements and calculations / Status text (info lines)
40750006 | Shore ¦ L-N unbalanced | Texts related to AC measurements and calculations / Status text (info lines)
40750007 | Shore ¦ L1-L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750008 | Shore ¦ L2-L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750009 | Shore ¦ L3-L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750010 | Shore ¦ L-L min. | Texts related to AC measurements and calculations / Status text (info lines)
40750011 | Shore ¦ L-L max. | Texts related to AC measurements and calculations / Status text (info lines)
40750012 | Shore ¦ L-L unbalanced | Texts related to AC measurements and calculations / Status text (info lines)
40750013 | Shore ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750014 | Shore ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750015 | Shore ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750016 | Shore ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40750017 | Shore ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40750018 | Shore ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40750019 | Shore ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40750020 | Shore ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750021 | Shore ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750022 | Shore ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750023 | Shore ¦ A-B phase angle L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750024 | Shore ¦ A-B phase angle L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750025 | Shore ¦ A-B phase angle L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750026 | Shore ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750027 | Shore ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750028 | Shore ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750029 | Shore ¦ N | Texts related to AC measurements and calculations / Status text (info lines)
40750030 | Shore ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40750031 | Shore ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40750032 | Shore ¦ Unbalanced nominal | Texts related to AC measurements and calculations / Status text (info lines)
40750033 | Shore ¦ Unbalanced average | Texts related to AC measurements and calculations / Status text (info lines)
40750034 | Shore ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750035 | Shore ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750036 | Shore ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750037 | Shore ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750038 | Shore ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750039 | Shore ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750040 | Shore ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40750041 | Shore ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40750042 | Shore ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40750043 | Shore ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750044 | Shore ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750045 | Shore ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750046 | Shore ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40750047 | Shore ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40750048 | Shore ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40750049 | Shore ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40750050 | Shore ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40750051 | Shore ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40750052 | Shore ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40750053 | Shore ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40750054 | Shore ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40750055 | Shore ¦ cos phi | Texts related to AC measurements and calculations / Status text (info lines)
40750056 | Shore ¦ Power factor | Texts related to AC measurements and calculations / Status text (info lines)
40750057 | Shore ¦ Positive sequence | Texts related to AC measurements and calculations / Status text (info lines)
40750058 | Shore ¦ Positive sequence | Texts related to AC measurements and calculations / Status text (info lines)
40750059 | Shore ¦ Negative sequence | Texts related to AC measurements and calculations / Status text (info lines)
40750060 | Shore ¦ Negative sequence | Texts related to AC measurements and calculations / Status text (info lines)
40750061 | Shore ¦ Zero sequence | Texts related to AC measurements and calculations / Status text (info lines)
40750062 | Shore ¦ Zero sequence | Texts related to AC measurements and calculations / Status text (info lines)
40750063 | Shore ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40750064 | Shore ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40750065 | Shore ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40750066 | Shore ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40750067 | Shore ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40750068 | Shore ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40750069 | Shore ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40750070 | Shore ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40750071 | Shore ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40750072 | Shore ¦ State | Texts related to AC measurements and calculations / Status text (info lines)
40760000 | Mains ¦ L1-N | Texts related to AC measurements and calculations / Used in view designs
40760001 | Mains ¦ L2-N | Texts related to AC measurements and calculations / Used in view designs
40760002 | Mains ¦ L3-N | Texts related to AC measurements and calculations / Used in view designs
40760003 | Mains ¦ N | Texts related to AC measurements and calculations / Used in view designs
40760004 | Mains ¦ L-N min. | Texts related to AC measurements and calculations / Used in view designs
40760005 | Mains ¦ L-N max. | Texts related to AC measurements and calculations / Used in view designs
40760006 | Mains ¦ L-N unbalanced | Texts related to AC measurements and calculations / Used in view designs
40760007 | Mains ¦ L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40760008 | Mains ¦ L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40760009 | Mains ¦ L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40760010 | Mains ¦ L-L min. | Texts related to AC measurements and calculations / Used in view designs
40760011 | Mains ¦ L-L max. | Texts related to AC measurements and calculations / Used in view designs
40760012 | Mains ¦ L-L unbalanced | Texts related to AC measurements and calculations / Used in view designs
40760013 | Mains ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40760014 | Mains ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40760015 | Mains ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40760016 | Mains ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40760017 | Mains ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40760018 | Mains ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40760019 | Mains ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40760020 | Mains ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40760021 | Mains ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40760022 | Mains ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40760023 | Mains ¦ A-B phase angle L1 | Texts related to AC measurements and calculations / Used in view designs
40760024 | Mains ¦ A-B phase angle L2 | Texts related to AC measurements and calculations / Used in view designs
40760025 | Mains ¦ A-B phase angle L3 | Texts related to AC measurements and calculations / Used in view designs
40760026 | Mains ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40760027 | Mains ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40760028 | Mains ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40760029 | Mains ¦ N | Texts related to AC measurements and calculations / Used in view designs
40760030 | Mains ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40760031 | Mains ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40760032 | Mains ¦ Unbalanced nominal | Texts related to AC measurements and calculations / Used in view designs
40760033 | Mains ¦ Unbalanced average | Texts related to AC measurements and calculations / Used in view designs
40760034 | Mains ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40760035 | Mains ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40760036 | Mains ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40760037 | Mains ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40760038 | Mains ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40760039 | Mains ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40760040 | Mains ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40760041 | Mains ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40760042 | Mains ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40760043 | Mains ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40760044 | Mains ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40760045 | Mains ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40760046 | Mains ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40760047 | Mains ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40760048 | Mains ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40760049 | Mains ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40760050 | Mains ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40760051 | Mains ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40760052 | Mains ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40760053 | Mains ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40760054 | Mains ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40760055 | Mains ¦ cos phi | Texts related to AC measurements and calculations / Used in view designs
40760056 | Mains ¦ Power factor | Texts related to AC measurements and calculations / Used in view designs
40760057 | Mains ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40760058 | Mains ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40760059 | Mains ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40760060 | Mains ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40760061 | Mains ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40760062 | Mains ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40760063 | Mains ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40760064 | Mains ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40760065 | Mains ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40760066 | Mains ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40760067 | Mains ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40760068 | Mains ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40760069 | Mains ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40760070 | Mains ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40760071 | Mains ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40760072 | Mains ¦ State | Texts related to AC measurements and calculations / Used in view designs
40770000 | Reference A ¦ L1-N | Texts related to AC measurements and calculations / Status text (info lines)
40770001 | Reference A ¦ L2-N | Texts related to AC measurements and calculations / Status text (info lines)
40770002 | Reference A ¦ L3-N | Texts related to AC measurements and calculations / Status text (info lines)
40770003 | Reference A ¦ N | Texts related to AC measurements and calculations / Status text (info lines)
40770004 | Reference A ¦ L-N min. | Texts related to AC measurements and calculations / Status text (info lines)
40770005 | Reference A ¦ L-N max. | Texts related to AC measurements and calculations / Status text (info lines)
40770006 | Reference A ¦ L-N unbalanced | Texts related to AC measurements and calculations / Status text (info lines)
40770007 | Reference A ¦ L1-L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770008 | Reference A ¦ L2-L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770009 | Reference A ¦ L3-L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770010 | Reference A ¦ L-L min. | Texts related to AC measurements and calculations / Status text (info lines)
40770011 | Reference A ¦ L-L max. | Texts related to AC measurements and calculations / Status text (info lines)
40770012 | Reference A ¦ L-L unbalanced | Texts related to AC measurements and calculations / Status text (info lines)
40770013 | Reference A ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770014 | Reference A ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770015 | Reference A ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770016 | Reference A ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40770017 | Reference A ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40770018 | Reference A ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40770019 | Reference A ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40770020 | Reference A ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770021 | Reference A ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770022 | Reference A ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770023 | Reference A ¦ Phase angle L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770024 | Reference A ¦ Phase angle L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770025 | Reference A ¦ Phase angle L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770026 | Reference A ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770027 | Reference A ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770028 | Reference A ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770029 | Reference A ¦ N | Texts related to AC measurements and calculations / Status text (info lines)
40770030 | Reference A ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40770031 | Reference A ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40770032 | Reference A ¦ Unbalanced nominal | Texts related to AC measurements and calculations / Status text (info lines)
40770033 | Reference A ¦ Unbalanced average | Texts related to AC measurements and calculations / Status text (info lines)
40770034 | Reference A ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770035 | Reference A ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770036 | Reference A ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770037 | Reference A ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770038 | Reference A ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770039 | Reference A ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770040 | Reference A ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40770041 | Reference A ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40770042 | Reference A ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40770043 | Reference A ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770044 | Reference A ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770045 | Reference A ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770046 | Reference A ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40770047 | Reference A ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40770048 | Reference A ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40770049 | Reference A ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40770050 | Reference A ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40770051 | Reference A ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40770052 | Reference A ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40770053 | Reference A ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40770054 | Reference A ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40770055 | Reference A ¦ cos phi | Texts related to AC measurements and calculations / Status text (info lines)
40770056 | Reference A ¦ Power factor | Texts related to AC measurements and calculations / Status text (info lines)
40770057 | Reference A ¦ Positive sequence | Texts related to AC measurements and calculations / Status text (info lines)
40770058 | Reference A ¦ Positive sequence | Texts related to AC measurements and calculations / Status text (info lines)
40770059 | Reference A ¦ Negative sequence | Texts related to AC measurements and calculations / Status text (info lines)
40770060 | Reference A ¦ Negative sequence | Texts related to AC measurements and calculations / Status text (info lines)
40770061 | Reference A ¦ Zero sequence | Texts related to AC measurements and calculations / Status text (info lines)
40770062 | Reference A ¦ Zero sequence | Texts related to AC measurements and calculations / Status text (info lines)
40770063 | Reference A ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40770064 | Reference A ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40770065 | Reference A ¦ Total | Texts related to AC measurements and calculations / Status text (info lines)
40770066 | Reference A ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40770067 | Reference A ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40770068 | Reference A ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40770069 | Reference A ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40770070 | Reference A ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40770071 | Reference A ¦ Available | Texts related to AC measurements and calculations / Status text (info lines)
40770072 | Reference A ¦ State | Texts related to AC measurements and calculations / Status text (info lines)
40780000 | Reference B ¦ L1-N | Texts related to AC measurements and calculations / Status text (info lines)
40780001 | Reference B ¦ L2-N | Texts related to AC measurements and calculations / Status text (info lines)
40780002 | Reference B ¦ L3-N | Texts related to AC measurements and calculations / Status text (info lines)
40780003 | Reference B ¦ N | Texts related to AC measurements and calculations / Status text (info lines)
40780004 | Reference B ¦ L-N min. | Texts related to AC measurements and calculations / Status text (info lines)
40780005 | Reference B ¦ L-N max. | Texts related to AC measurements and calculations / Status text (info lines)
40780006 | Reference B ¦ L-N unbalanced | Texts related to AC measurements and calculations / Status text (info lines)
40780007 | Reference B ¦ L1-L2 | Texts related to AC measurements and calculations / Status text (info lines)
40780008 | Reference B ¦ L2-L3 | Texts related to AC measurements and calculations / Status text (info lines)
40780009 | Reference B ¦ L3-L1 | Texts related to AC measurements and calculations / Status text (info lines)
40780010 | Reference B ¦ L-L min. | Texts related to AC measurements and calculations / Status text (info lines)
40780011 | Reference B ¦ L-L max. | Texts related to AC measurements and calculations / Status text (info lines)
40780012 | Reference B ¦ L-L unbalanced | Texts related to AC measurements and calculations / Status text (info lines)
40780013 | Reference B ¦ L1 | Texts related to AC measurements and calculations / Status text (info lines)
40780014 | Reference B ¦ L2 | Texts related to AC measurements and calculations / Status text (info lines)
40780015 | Reference B ¦ L3 | Texts related to AC measurements and calculations / Status text (info lines)
40780016 | Reference B ¦ Min. | Texts related to AC measurements and calculations / Status text (info lines)
40780017 | Reference B ¦ Max. | Texts related to AC measurements and calculations / Status text (info lines)
40780020 | Reference B ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Status text (info lines)
40780021 | Reference B ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Status text (info lines)
40780022 | Reference B ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Status text (info lines)
40780057 | Reference B ¦ Positive sequence | Texts related to AC measurements and calculations / Status text (info lines)
40780059 | Reference B ¦ Negative sequence | Texts related to AC measurements and calculations / Status text (info lines)
40780061 | Reference B ¦ Zero sequence | Texts related to AC measurements and calculations / Status text (info lines)
40780062 | Reference B ¦ State | Texts related to AC measurements and calculations / Status text (info lines)
40790000 | Inverter ¦ L1-N | Texts related to AC measurements and calculations / Used in view designs
40790001 | Inverter ¦ L2-N | Texts related to AC measurements and calculations / Used in view designs
40790002 | Inverter ¦ L3-N | Texts related to AC measurements and calculations / Used in view designs
40790003 | Inverter ¦ N | Texts related to AC measurements and calculations / Used in view designs
40790004 | Inverter ¦ L-N min. | Texts related to AC measurements and calculations / Used in view designs
40790005 | Inverter ¦ L-N max. | Texts related to AC measurements and calculations / Used in view designs
40790006 | Inverter ¦ L-N unbalanced | Texts related to AC measurements and calculations / Used in view designs
40790007 | Inverter ¦ L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40790008 | Inverter ¦ L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40790009 | Inverter ¦ L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40790010 | Inverter ¦ L-L min. | Texts related to AC measurements and calculations / Used in view designs
40790011 | Inverter ¦ L-L max. | Texts related to AC measurements and calculations / Used in view designs
40790012 | Inverter ¦ L-L unbalanced | Texts related to AC measurements and calculations / Used in view designs
40790013 | Inverter ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40790014 | Inverter ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40790015 | Inverter ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40790016 | Inverter ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40790017 | Inverter ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40790018 | Inverter ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40790019 | Inverter ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40790020 | Inverter ¦ Phase angle L1-L2 | Texts related to AC measurements and calculations / Used in view designs
40790021 | Inverter ¦ Phase angle L2-L3 | Texts related to AC measurements and calculations / Used in view designs
40790022 | Inverter ¦ Phase angle L3-L1 | Texts related to AC measurements and calculations / Used in view designs
40790023 | Inverter ¦ A-B phase angle L1 | Texts related to AC measurements and calculations / Used in view designs
40790024 | Inverter ¦ A-B phase angle L2 | Texts related to AC measurements and calculations / Used in view designs
40790025 | Inverter ¦ A-B phase angle L3 | Texts related to AC measurements and calculations / Used in view designs
40790026 | Inverter ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40790027 | Inverter ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40790028 | Inverter ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40790029 | Inverter ¦ N | Texts related to AC measurements and calculations / Used in view designs
40790030 | Inverter ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40790031 | Inverter ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40790032 | Inverter ¦ Unbalanced nominal | Texts related to AC measurements and calculations / Used in view designs
40790033 | Inverter ¦ Unbalanced average | Texts related to AC measurements and calculations / Used in view designs
40790034 | Inverter ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40790035 | Inverter ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40790036 | Inverter ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40790037 | Inverter ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40790038 | Inverter ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40790039 | Inverter ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40790040 | Inverter ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40790041 | Inverter ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40790042 | Inverter ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40790043 | Inverter ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40790044 | Inverter ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40790045 | Inverter ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40790046 | Inverter ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40790047 | Inverter ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40790048 | Inverter ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40790049 | Inverter ¦ L1 | Texts related to AC measurements and calculations / Used in view designs
40790050 | Inverter ¦ L2 | Texts related to AC measurements and calculations / Used in view designs
40790051 | Inverter ¦ L3 | Texts related to AC measurements and calculations / Used in view designs
40790052 | Inverter ¦ Min. | Texts related to AC measurements and calculations / Used in view designs
40790053 | Inverter ¦ Max. | Texts related to AC measurements and calculations / Used in view designs
40790054 | Inverter ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40790055 | Inverter ¦ cos phi | Texts related to AC measurements and calculations / Used in view designs
40790056 | Inverter ¦ Power factor | Texts related to AC measurements and calculations / Used in view designs
40790057 | Inverter ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40790058 | Inverter ¦ Positive sequence | Texts related to AC measurements and calculations / Used in view designs
40790059 | Inverter ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40790060 | Inverter ¦ Negative sequence | Texts related to AC measurements and calculations / Used in view designs
40790061 | Inverter ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40790062 | Inverter ¦ Zero sequence | Texts related to AC measurements and calculations / Used in view designs
40790063 | Inverter ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40790064 | Inverter ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40790065 | Inverter ¦ Total | Texts related to AC measurements and calculations / Used in view designs
40790066 | Inverter ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40790067 | Inverter ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40790068 | Inverter ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40790069 | Inverter ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40790070 | Inverter ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40790071 | Inverter ¦ Available | Texts related to AC measurements and calculations / Used in view designs
40790072 | Inverter ¦ State | Texts related to AC measurements and calculations / Used in view designs
40790100 | Inverter ¦ L1 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40790101 | Inverter ¦ L2 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40790102 | Inverter ¦ L3 (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40790103 | Inverter ¦ Min. (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40790104 | Inverter ¦ Max. (Consumer side) | Texts related to AC measurements and calculations / Used in view designs
40790110 | Inverter ¦ L1 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40790111 | Inverter ¦ L2 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40790112 | Inverter ¦ L3 (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40790113 | Inverter ¦ Min. (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40790114 | Inverter ¦ Max. (Neutral side) | Texts related to AC measurements and calculations / Used in view designs
40790120 | Inverter ¦ L1 differential | Texts related to AC measurements and calculations / Used in view designs
40790121 | Inverter ¦ L2 differential | Texts related to AC measurements and calculations / Used in view designs
40790122 | Inverter ¦ L3 differential | Texts related to AC measurements and calculations / Used in view designs
40790123 | Inverter ¦ Min. differential | Texts related to AC measurements and calculations / Used in view designs
40790124 | Inverter ¦ Max. differential | Texts related to AC measurements and calculations / Used in view designs
40790130 | Inverter ¦ L1 restraint | Texts related to AC measurements and calculations / Used in view designs
40790131 | Inverter ¦ L2 restraint | Texts related to AC measurements and calculations / Used in view designs
40790132 | Inverter ¦ L3 restraint | Texts related to AC measurements and calculations / Used in view designs
40790133 | Inverter ¦ Min. restraint | Texts related to AC measurements and calculations / Used in view designs
40790134 | Inverter ¦ Max. restraint | Texts related to AC measurements and calculations / Used in view designs
40790140 | Inverter ¦ Frequency | Texts related to AC measurements and calculations / Used in view designs
40800000 | Voltage | Texts related to AC measurements and calculations / Parameter name
40800010 | Current | Texts related to AC measurements and calculations / Parameter name
40800020 | Active power | Texts related to AC measurements and calculations / Parameter name
40800030 | Reactive power | Texts related to AC measurements and calculations / Parameter name
40800040 | Apparent power | Texts related to AC measurements and calculations / Parameter name
40800050 | Power factor and cos phi | Texts related to AC measurements and calculations / Parameter name
40800060 | Frequency from voltage | Texts related to AC measurements and calculations / Parameter name
40800070 | Frequency from current | Texts related to AC measurements and calculations / Parameter name
40810000 | No filter | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40810001 | Averaged (200 ms) | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
40810002 | Averaged (800 ms) | Texts related to AC measurements and calculations / Parameter configuration (selected from a list)
45001010 | ROCOF (df/dt) | Texts regarding AC protections / Label text
45001020 | Vector shift | Texts regarding AC protections / Label text
45001030 | Inverse time over-current | Texts regarding AC protections / Label text
45001040 | Earth inverse time over-current | Texts regarding AC protections / Label text
45001050 | Neutral inverse time over-current | Texts regarding AC protections / Label text
45001060 | Voltage-dependent over-current | Texts regarding AC protections / Label text
45001090 | Power-dependent Q< | Texts regarding AC protections / Label text
45001100 | Power-dependent Q> | Texts regarding AC protections / Label text
45001110 | V< and Q< 1 | Texts regarding AC protections / Label text
45001120 | V< and Q< 2 | Texts regarding AC protections / Label text
45001130 | Average over-voltage 1 | Texts regarding AC protections / Label text
45001140 | Average over-voltage 2 | Texts regarding AC protections / Label text
45001150 | Time-dependent under-voltage 1 | Texts regarding AC protections / Label text
45001160 | Time-dependent under-voltage 2 | Texts regarding AC protections / Label text
45001170 | Time-dependent under-voltage 3 | Texts regarding AC protections / Label text
45001180 | Aggregation time | Texts regarding AC protections / Label text
45001190 | Aggregation interval | Texts regarding AC protections / Label text
45001200 | Protection set point out of range (ACM3.1) | Texts regarding AC protections / Label text
45001210 | Stabilised differential | Texts regarding AC protections / Label text
45001220 | High set differential | Texts regarding AC protections / Label text
45001230 | Protection set point out of range (ACM3.2) | Texts regarding AC protections / Label text
45101200 | Phase-phase busbar | Texts regarding AC protections / Miscellaneous text (various uses)
45101210 | Phase-neutral busbar | Texts regarding AC protections / Miscellaneous text (various uses)
45101220 | Phase-phase generator | Texts regarding AC protections / Miscellaneous text (various uses)
45101230 | Phase-neutral generator | Texts regarding AC protections / Miscellaneous text (various uses)
45101240 | Phase-phase mains | Texts regarding AC protections / Miscellaneous text (various uses)
45101250 | Phase-neutral mains | Texts regarding AC protections / Miscellaneous text (various uses)
45101260 | Phase-phase busbar A | Texts regarding AC protections / Miscellaneous text (various uses)
45101270 | Phase-neutral busbar A | Texts regarding AC protections / Miscellaneous text (various uses)
45101280 | Phase-phase busbar B | Texts regarding AC protections / Miscellaneous text (various uses)
45101290 | Phase-neutral busbar B | Texts regarding AC protections / Miscellaneous text (various uses)
45101300 | Busbar | Texts regarding AC protections / Miscellaneous text (various uses)
45101310 | Busbar A | Texts regarding AC protections / Miscellaneous text (various uses)
45101320 | Busbar B | Texts regarding AC protections / Miscellaneous text (various uses)
45101330 | Generator | Texts regarding AC protections / Miscellaneous text (various uses)
45101340 | Mains | Texts regarding AC protections / Miscellaneous text (various uses)
45300030 | ROCOF (df/dt) period | Texts regarding AC protections / Parameter name
45300050 | Vector shift select | Texts regarding AC protections / Parameter name
45300070 | Curve | Texts regarding AC protections / Parameter name
45300080 | Limit | Texts regarding AC protections / Parameter name
45300090 | Time multiplier setting | Texts regarding AC protections / Parameter name
45300130 | k | Texts regarding AC protections / Parameter name
45300140 | c | Texts regarding AC protections / Parameter name
45300150 | alpha | Texts regarding AC protections / Parameter name
45300170 | Curve | Texts regarding AC protections / Parameter name
45300180 | Limit | Texts regarding AC protections / Parameter name
45300190 | Time multiplier setting | Texts regarding AC protections / Parameter name
45300230 | k | Texts regarding AC protections / Parameter name
45300240 | c | Texts regarding AC protections / Parameter name
45300250 | alpha | Texts regarding AC protections / Parameter name
45300270 | Curve | Texts regarding AC protections / Parameter name
45300280 | Limit | Texts regarding AC protections / Parameter name
45300290 | Time multiplier setting | Texts regarding AC protections / Parameter name
45300330 | k | Texts regarding AC protections / Parameter name
45300340 | c | Texts regarding AC protections / Parameter name
45300350 | alpha | Texts regarding AC protections / Parameter name
45300370 | V (50%) dependent I> | Texts regarding AC protections / Parameter name
45300380 | V (60%) dependent I> | Texts regarding AC protections / Parameter name
45300390 | V (70%) dependent I> | Texts regarding AC protections / Parameter name
45300400 | V (80%) dependent I> | Texts regarding AC protections / Parameter name
45300410 | V (90%) dependent I> | Texts regarding AC protections / Parameter name
45300420 | V (100%) dependent I> | Texts regarding AC protections / Parameter name
45300430 | Threshold | Texts regarding AC protections / Parameter name
45300440 | Threshold | Texts regarding AC protections / Parameter name
45300450 | Threshold | Texts regarding AC protections / Parameter name
45300950 | I min. | Texts regarding AC protections / Parameter name
45300960 | Angle min. | Texts regarding AC protections / Parameter name
45300970 | I min. | Texts regarding AC protections / Parameter name
45300980 | Angle min. | Texts regarding AC protections / Parameter name
45301020 | V> aggregate time | Texts regarding AC protections / Timer text
45301040 | V> aggregate time | Texts regarding AC protections / Timer text
45301100 | ROCOF (df/dt) measurement half period | Texts regarding AC protections / Timer text
45301110 | ROCOF (df/dt) positive set point | Texts regarding AC protections / Parameter name
45301120 | ROCOF (df/dt) negative set point | Texts regarding AC protections / Parameter name
45301130 | Measure mode | Texts regarding AC protections / Parameter name
45350000 | Graph | Texts regarding AC protections / Parameter name
45350010 | I diff. min. | Texts regarding AC protections / Parameter name
45350020 | Region 1: End | Texts regarding AC protections / Parameter name
45350030 | Region 2: Slope | Texts regarding AC protections / Parameter name
45350040 | Region 2: End | Texts regarding AC protections / Parameter name
45350050 | Region 3: Slope | Texts regarding AC protections / Parameter name
45400001 | ROCOF (df/dt) | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400002 | Vector shift | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400003 | Inverse time over-current | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400004 | Earth inverse time over-current | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400005 | Neutral inverse time over-current | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400006 | Voltage-dependent over-current | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400009 | Power-dependent Q low | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400010 | Power-dependent Q high | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400011 | Q-dependent under-voltage 1 | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400012 | Q-dependent under-voltage 2 | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400013 | Average over-voltage 1 | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400014 | Average over-voltage 2 | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400015 | Time-dependent under-voltage 1 | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400016 | Time-dependent under-voltage 2 | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45400017 | Time-dependent under-voltage 3 | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45420000 | Stabilised differential | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45420001 | High set differential | Texts regarding AC protections / Assignable function (input/output config menus, Modbus)
45600000 | Zero sequence current | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600001 | Zero sequence voltage | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600002 | Negative sequence current | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600003 | Negative sequence voltage | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600004 | Current unbalance (nominal calc.) | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600005 | Current unbalance (average calc.) | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600006 | Generator voltage unbalance | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600007 | Busbar voltage unbalance | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600008 | Reactive power import 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600009 | Reactive power import 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600010 | Reactive power export 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600011 | Reactive power export 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600012 | Reverse power 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600013 | Reverse power 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600014 | Overload 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600015 | Overload 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600016 | Busbar under-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600017 | Busbar under-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600018 | Busbar over-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600019 | Busbar over-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600020 | Busbar under-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600021 | Busbar under-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600022 | Busbar over-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600023 | Busbar over-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600024 | Generator under-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600025 | Generator under-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600026 | Generator over-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600027 | Generator over-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600028 | Generator under-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600029 | Generator under-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600030 | Generator over-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600031 | Generator over-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600032 | Directional over-current 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600033 | Directional over-current 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600034 | Fast over-current 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600035 | Fast over-current 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600036 | Over-current 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600037 | Over-current 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600038 | Busbar under-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600039 | Busbar under-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600040 | Busbar over-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600041 | Busbar over-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600042 | Busbar under-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600043 | Busbar under-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600044 | Busbar over-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600045 | Busbar over-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600046 | Shore connection under-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600047 | Shore connection under-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600048 | Shore connection over-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600049 | Shore connection over-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600050 | Shore connection under-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600051 | Shore connection under-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600052 | Shore connection over-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600053 | Shore connection over-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600054 | Shore connection voltage unbalance | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600055 | Busbar voltage unbalance | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600056 | Busbar A under-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600057 | Busbar A under-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600058 | Busbar A over-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600059 | Busbar A over-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600060 | Busbar A under-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600061 | Busbar A under-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600062 | Busbar A over-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600063 | Busbar A over-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600064 | Busbar B under-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600065 | Busbar B under-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600066 | Busbar B over-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600067 | Busbar B over-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600068 | Busbar B under-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600069 | Busbar B under-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600070 | Busbar B over-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600071 | Busbar B over-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600072 | Busbar A voltage unbalance | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600073 | Busbar B voltage unbalance | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600074 | Positive sequence under-voltage | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600075 | Busbar over-voltage 1 average | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600076 | Busbar over-voltage 2 average | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600077 | Mains under-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600078 | Mains under-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600079 | Mains over-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600080 | Mains over-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600081 | Mains under-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600082 | Mains under-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600083 | Mains over-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600084 | Mains over-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600085 | Mains voltage unbalance | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600086 | Mains over-voltage 1 average | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600087 | Mains over-voltage 2 average | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600088 | Directional over-current 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600089 | Directional over-current 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600090 | AC setup | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600091 | Power import 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600092 | Power import 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600093 | Power export 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600094 | Power export 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600095 | Overload reverse power 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600096 | Overload reverse power 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600097 | Inverter under-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600098 | Inverter under-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600099 | Inverter over-frequency 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600100 | Inverter over-frequency 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600101 | Inverter under-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600102 | Inverter under-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600103 | Inverter over-voltage 2 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600104 | Inverter over-voltage 1 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600105 | Inverter voltage unbalance | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600106 | Over-current 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600107 | Over-current 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600108 | Generator under-voltage 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600109 | Generator over-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600110 | Generator under-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600111 | Busbar over-voltage 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600112 | Busbar under-voltage 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600113 | Busbar under-voltage 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600114 | Busbar over-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600115 | Busbar under-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600116 | Busbar under-frequency 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600117 | Overload 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600118 | Overload 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600119 | Overload 5 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600120 | Mains over-voltage 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600121 | Mains under-voltage 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600122 | Mains under-voltage 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600123 | Mains over-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600124 | Mains under-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600125 | Mains under-frequency 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600126 | Busbar A under-voltage 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600127 | Busbar A over-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600128 | Busbar A under-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600129 | Busbar B over-voltage 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600130 | Busbar B under-voltage 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600131 | Busbar B under-voltage 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600132 | Busbar B over-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600133 | Busbar B under-frequency 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600134 | Busbar B under-frequency 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600135 | Power export 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600136 | Power export 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600137 | Power export 5 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600138 | Power import 3 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600139 | Power import 4 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45600140 | Power import 5 | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601032 | Individual phases | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601033 | All phases | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601034 | IEC inverse | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601035 | IEC very inverse | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601036 | IEC extremely inverse | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601037 | IEEE moderately inverse | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601038 | IEEE very inverse | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601039 | IEEE extremely inverse | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601040 | Custom characteristic | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601041 | Exactly 1 of 3 phases | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601042 | Exactly 2 of 3 phases | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601043 | Exactly 3 of 3 phases | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601044 | 1 or more phases | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601045 | LVRT x-axis | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601046 | LVRT y-axis | Texts regarding AC protections / Alarm text (pop-ups and logs)
45601047 | External fault-ride-through configure error | Texts regarding AC protections / Alarm text (pop-ups and logs)
45620000 | Restraint current | Texts regarding AC protections / Alarm text (pop-ups and logs)
45620001 | Differential current | Texts regarding AC protections / Alarm text (pop-ups and logs)
45620002 | High set differential | Texts regarding AC protections / Alarm text (pop-ups and logs)
45800000 | Normal | Texts regarding AC protections / Parameter name
45800001 | G59/3 | Texts regarding AC protections / Parameter name
45800010 | Activation threshold | Texts regarding AC protections / Parameter name
45800011 | Deactivation threshold | Texts regarding AC protections / Parameter name
45800012 | Number of start phases | Texts regarding AC protections / Parameter name
45800013 | Deactivation recovery delay | Texts regarding AC protections / Parameter name
45800014 | Minimum active time | Texts regarding AC protections / Parameter name
45800015 | Suspend regulator delay | Texts regarding AC protections / Parameter name
45800016 | Graph | Texts regarding AC protections / Parameter name
60000000 | Current PMS mode | General information and announcements to user / Parameter name
60000010 | Previous PMS mode | General information and announcements to user / Parameter name
60000100 | PICUS commands | General information and announcements to user / Parameter name
60000110 | Display commands | General information and announcements to user / Parameter name
60000120 | Modbus commands | General information and announcements to user / Parameter name
60000130 | I/O commands | General information and announcements to user / Parameter name
60000140 | CustomLogic commands | General information and announcements to user / Parameter name
60000150 | CODESYS commands | General information and announcements to user / Parameter name
60000160 | Display commands | General information and announcements to user / Parameter name
60000300 | PICUS commands | General information and announcements to user / Parameter name
60000310 | Display commands | General information and announcements to user / Parameter name
60000320 | Modbus commands | General information and announcements to user / Parameter name
60000330 | I/O commands | General information and announcements to user / Parameter name
60000340 | CustomLogic commands | General information and announcements to user / Parameter name
60000350 | CODESYS commands | General information and announcements to user / Parameter name
60000360 | Display commands | General information and announcements to user / Parameter name
60000400 | Display commands | General information and announcements to user / Parameter name
60000500 | MANUAL | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000501 | AUTO | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000502 | Current PMS mode | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000503 | In AUTO | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000504 | In MANUAL | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000505 | Local control | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000506 | Remote control | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000507 | Under local control | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000508 | Under remote control | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000509 | Current control | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000510 | Block | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000511 | Test | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000512 | No regulation | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60000601 | Manual | General information and announcements to user / Status text (info lines)
60000602 | Auto | General information and announcements to user / Status text (info lines)
60000603 | No mode change | General information and announcements to user / Status text (info lines)
60000604 | Mode change locked | General information and announcements to user / Status text (info lines)
60000605 | Start/Stop engine | General information and announcements to user / Status text (info lines)
60000606 | Start/Stop inverter | General information and announcements to user / Status text (info lines)
60000607 | Open/Close generator breaker | General information and announcements to user / Status text (info lines)
60000608 | Open/Close tie breaker | General information and announcements to user / Status text (info lines)
60000609 | Open/Close bus tie breaker | General information and announcements to user / Status text (info lines)
60000610 | Open/Close shaft breaker | General information and announcements to user / Status text (info lines)
60000611 | Open/Close shore breaker | General information and announcements to user / Status text (info lines)
60000612 | Open/Close inverter breaker | General information and announcements to user / Status text (info lines)
60000613 | Open/Close mains breaker | General information and announcements to user / Status text (info lines)
60000614 | Manual/Auto mode | General information and announcements to user / Status text (info lines)
60000615 | First priority | General information and announcements to user / Status text (info lines)
60000616 | Mute alarm | General information and announcements to user / Status text (info lines)
60000617 | Test engine | General information and announcements to user / Status text (info lines)
60000618 | Remote/Local | General information and announcements to user / Status text (info lines)
60000619 | Buttons are disabled | General information and announcements to user / Status text (info lines)
60000620 | Start/Stop | General information and announcements to user / Status text (info lines)
60000622 | Remote control | General information and announcements to user / Status text (info lines)
60000623 | Local control | General information and announcements to user / Status text (info lines)
60000624 | Service not permitted | General information and announcements to user / Status text (info lines)
60000625 | Enter service GB close inhibit | General information and announcements to user / Status text (info lines)
60000626 | Enter service OK in | General information and announcements to user / Status text (info lines)
60000700 | Not under remote control | General information and announcements to user / Alarm text (pop-ups and logs)
60000701 | Not under remote control | General information and announcements to user / Alarm text (pop-ups and logs)
60000800 | MANUAL | General information and announcements to user / Event text (pop-ups, logs and status texts)
60000810 | Inhibit Modbus command | General information and announcements to user / Event text (pop-ups, logs and status texts)
60000820 | Enter service GB block | General information and announcements to user / Event text (pop-ups, logs and status texts)
60010000 | De-energise when all alarms are acknowledged | General information and announcements to user / Parameter name
60010010 | Reset when new alarm | General information and announcements to user / Parameter name
60010020 | Minimum down time | General information and announcements to user / Parameter name
60010030 | Minimum up time | General information and announcements to user / Parameter name
60010040 | Horn 1 | General information and announcements to user / Parameter name
60010100 | De-energise when all alarms are acknowledged | General information and announcements to user / Parameter name
60010110 | Reset when new alarm | General information and announcements to user / Parameter name
60010120 | Minimum down time | General information and announcements to user / Parameter name
60010130 | Minimum up time | General information and announcements to user / Parameter name
60010140 | Horn 2 | General information and announcements to user / Parameter name
60010200 | De-energise when all alarms are acknowledged | General information and announcements to user / Parameter name
60010210 | Reset when new alarm | General information and announcements to user / Parameter name
60010220 | Minimum down time | General information and announcements to user / Parameter name
60010230 | Minimum up time | General information and announcements to user / Parameter name
60010240 | Horn 3 | General information and announcements to user / Parameter name
60010300 | Status OK | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60010310 | Card OK input | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60010320 | Duty cycle | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60010330 | Period | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60010340 | On time | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60010350 | Alive | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60025000 | Activate inhibit 1 | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60025001 | Activate inhibit 2 | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60025002 | Activate inhibit 3 | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60025005 | Activate inhibit 4 | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60025006 | Activate inhibit 5 | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60025007 | Activate inhibit 6 | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60025008 | Activate inhibit 7 | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60025009 | Activate inhibit 8 | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60027000 | Engine running | General information and announcements to user / Parameter name
60027001 | Engine not running | General information and announcements to user / Parameter name
60027002 | Inhibit 1 | General information and announcements to user / Parameter name
60027003 | Inhibit 2 | General information and announcements to user / Parameter name
60027004 | Inhibit 3 | General information and announcements to user / Parameter name
60027005 | Generator breaker open | General information and announcements to user / Parameter name
60027006 | Generator breaker closed | General information and announcements to user / Parameter name
60027007 | Generator voltage present | General information and announcements to user / Parameter name
60027008 | No generator voltage | General information and announcements to user / Parameter name
60027009 | Generator frequency present | General information and announcements to user / Parameter name
60027010 | No generator frequency | General information and announcements to user / Parameter name
60027011 | Power take home active | General information and announcements to user / Parameter name
60027012 | Shaft breaker open | General information and announcements to user / Parameter name
60027013 | Shaft breaker closed | General information and announcements to user / Parameter name
60027014 | Shore connection breaker open | General information and announcements to user / Parameter name
60027015 | Shore connection breaker closed | General information and announcements to user / Parameter name
60027016 | Bus tie breaker open | General information and announcements to user / Parameter name
60027017 | Bus tie breaker closed | General information and announcements to user / Parameter name
60027018 | Tie breaker open | General information and announcements to user / Parameter name
60027019 | Tie breaker closed | General information and announcements to user / Parameter name
60027020 | Controller under SWBD control | General information and announcements to user / Parameter name
60027021 | ACM wire break | General information and announcements to user / Parameter name
60027022 | EDG in parallel | General information and announcements to user / Parameter name
60027023 | EDG handling blackout | General information and announcements to user / Parameter name
60027024 | Shore voltage present | General information and announcements to user / Parameter name
60027025 | No shore voltage | General information and announcements to user / Parameter name
60027026 | Shore frequency present | General information and announcements to user / Parameter name
60027027 | No shore frequency | General information and announcements to user / Parameter name
60027028 | Ship-to-ship active | General information and announcements to user / Parameter name
60027029 | Busbar A voltage present | General information and announcements to user / Parameter name
60027030 | No busbar A voltage | General information and announcements to user / Parameter name
60027031 | Busbar A frequency present | General information and announcements to user / Parameter name
60027032 | No busbar A frequency | General information and announcements to user / Parameter name
60027033 | Busbar B voltage present | General information and announcements to user / Parameter name
60027034 | No busbar B voltage | General information and announcements to user / Parameter name
60027035 | Busbar B frequency present | General information and announcements to user / Parameter name
60027036 | No busbar B frequency | General information and announcements to user / Parameter name
60027037 | Mains breaker open | General information and announcements to user / Parameter name
60027038 | Mains breaker closed | General information and announcements to user / Parameter name
60027039 | Mains in parallel | General information and announcements to user / Parameter name
60027040 | Mains not in parallel | General information and announcements to user / Parameter name
60027041 | Mains voltage present | General information and announcements to user / Parameter name
60027042 | No mains voltage | General information and announcements to user / Parameter name
60027043 | Mains frequency present | General information and announcements to user / Parameter name
60027044 | No mains frequency | General information and announcements to user / Parameter name
60027045 | Genset in parallel | General information and announcements to user / Parameter name
60027046 | Genset not in parallel | General information and announcements to user / Parameter name
60027047 | Engine stopping | General information and announcements to user / Parameter name
60027048 | Inverter running | General information and announcements to user / Parameter name
60027049 | Inverter not running | General information and announcements to user / Parameter name
60027050 | Inverter stopping | General information and announcements to user / Parameter name
60027051 | Operating mode PTI (power take in) | General information and announcements to user / Parameter name
60027052 | Operating mode PTO (power take off) | General information and announcements to user / Parameter name
60027053 | Operating mode standby | General information and announcements to user / Parameter name
60027054 | Idle run active | General information and announcements to user / Parameter name
60027055 | Breaker open | General information and announcements to user / Parameter name
60027056 | Breaker closed | General information and announcements to user / Parameter name
60027057 | Inverter voltage present | General information and announcements to user / Parameter name
60027058 | No inverter voltage | General information and announcements to user / Parameter name
60027059 | Inverter frequency present | General information and announcements to user / Parameter name
60027060 | No inverter frequency | General information and announcements to user / Parameter name
60027061 | Inhibit 4 | General information and announcements to user / Parameter name
60027062 | Inhibit 5 | General information and announcements to user / Parameter name
60027063 | Inhibit 6 | General information and announcements to user / Parameter name
60027064 | Inhibit 7 | General information and announcements to user / Parameter name
60027065 | Inhibit 8 | General information and announcements to user / Parameter name
60030000 | Enable alarm test | General information and announcements to user / Parameter name
60030010 | Test type | General information and announcements to user / Parameter name
60030020 | Trip AVR output not configured | General information and announcements to user / Parameter name
60034000 | Alarm test event | General information and announcements to user / Event text (pop-ups, logs and status texts)
60034100 | Suppress alarm action enabled | General information and announcements to user / Event text (pop-ups, logs and status texts)
60034110 | Suppress alarm action disabled | General information and announcements to user / Event text (pop-ups, logs and status texts)
60035000 | Acknowledge all alarms | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035001 | Reset all latched alarms | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035002 | Number of alarms | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035003 | Number of unacknowledged alarms | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035004 | Number of acknowledged alarms | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035005 | Any warning alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035006 | Any block alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035007 | Any PMS controlled stop alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035008 | Any trip alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035009 | Any trip and stop alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035010 | Any trip and shutdown alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035011 | Any TB trip alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035012 | Any BTB trip alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035013 | Any stop alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035014 | Any alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035015 | Any unacknowledged alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035016 | Any latched alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035017 | Any shelved alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035018 | Any out of service alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035019 | Any MB trip alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035020 | Any MB and TB trip alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035021 | Any MB block alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035022 | Any GB and MB trip alarms | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035023 | Any AVR alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035024 | Any trip + AVR alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035025 | Any trip + AVR + stop alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035026 | Any trip + AVR + shutdown alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035027 | Any controlled stop alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035028 | Any TB block alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035029 | Any MB and TB trip alarms | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035030 | Suppress alarm action | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035033 | Reset horn | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035035 | Any default action alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035036 | Any action 1 alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035037 | Any action 2 alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035038 | Any action 3 alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035039 | Any action 4 alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035040 | Any action 5 alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035041 | Any action 6 alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035042 | Any action 7 alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60035043 | Any action 8 alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60036000 | All alarms | General information and announcements to user / Parameter name
60036001 | Enabled alarms | General information and announcements to user / Parameter name
60036002 | Alarm testing | General information and announcements to user / Parameter name
60037000 | Block | General information and announcements to user / Alarm action
60037001 | Warning | General information and announcements to user / Alarm action
60037002 | Trip generator breaker | General information and announcements to user / Alarm action
60037003 | Trip generator breaker and stop engine | General information and announcements to user / Alarm action
60037004 | Trip tie breaker | General information and announcements to user / Alarm action
60037005 | Trip bus tie breaker | General information and announcements to user / Alarm action
60037006 | Trip generator breaker | General information and announcements to user / Alarm action
60037007 | Trip shore connection breaker | General information and announcements to user / Alarm action
60037008 | Trip generator breaker and shutdown engine | General information and announcements to user / Alarm action
60037009 | PMS-controlled stop | General information and announcements to user / Alarm action
60037010 | PMS-controlled open breaker | General information and announcements to user / Alarm action
60037011 | Trip mains breaker | General information and announcements to user / Alarm action
60037012 | Trip mains and tie breaker | General information and announcements to user / Alarm action
60037013 | Block mains breaker | General information and announcements to user / Alarm action
60037014 | Trip generator and main breakers | General information and announcements to user / Alarm action
60037015 | Block generator breaker | General information and announcements to user / Alarm action
60037016 | Block bus tie breaker | General information and announcements to user / Alarm action
60037017 | Open shore connection breaker | General information and announcements to user / Alarm action
60037018 | Operator select | General information and announcements to user / Alarm action
60037019 | Open without de-loading | General information and announcements to user / Alarm action
60037020 | Trip AVR | General information and announcements to user / Alarm action
60037021 | Trip generator breaker + AVR | General information and announcements to user / Alarm action
60037022 | Trip generator breaker + AVR | General information and announcements to user / Alarm action
60037023 | Trip generator breaker + AVR + stop engine | General information and announcements to user / Alarm action
60037024 | Trip generator breaker + AVR + shutdown engine | General information and announcements to user / Alarm action
60037025 | Trip breaker | General information and announcements to user / Alarm action
60037026 | Trip breaker and stop inverter | General information and announcements to user / Alarm action
60037027 | Trip breaker + AVR | General information and announcements to user / Alarm action
60037028 | Trip breaker + AVR + stop inverter | General information and announcements to user / Alarm action
60037029 | Stop inverter | General information and announcements to user / Alarm action
60037030 | Controlled stop | General information and announcements to user / Alarm action
60037031 | Block tie breaker | General information and announcements to user / Alarm action
60037032 | Default action | General information and announcements to user / Alarm action
60037033 | Action 1 | General information and announcements to user / Alarm action
60037034 | Action 2 | General information and announcements to user / Alarm action
60037035 | Action 3 | General information and announcements to user / Alarm action
60037036 | Action 4 | General information and announcements to user / Alarm action
60037037 | Action 5 | General information and announcements to user / Alarm action
60037038 | Action 6 | General information and announcements to user / Alarm action
60037039 | Action 7 | General information and announcements to user / Alarm action
60037040 | Action 8 | General information and announcements to user / Alarm action
60037100 | Any GB trip alarm | General information and announcements to user / Alarm action
60037101 | Any SGB trip alarm | General information and announcements to user / Alarm action
60037102 | Any SCB trip alarm | General information and announcements to user / Alarm action
60037103 | Any BTB trip alarm | General information and announcements to user / Alarm action
60037104 | Any TB trip alarm | General information and announcements to user / Alarm action
60037105 | Any GB trip and stop alarm | General information and announcements to user / Alarm action
60037106 | Any GB trip and shutdown alarm | General information and announcements to user / Alarm action
60037107 | Any PMS-controlled stop alarm | General information and announcements to user / Alarm action
60037108 | Any PMS-controlled open breaker alarm | General information and announcements to user / Alarm action
60037109 | Any MB trip alarm | General information and announcements to user / Alarm action
60037110 | Any MB and TB trip alarm | General information and announcements to user / Alarm action
60037111 | Any GB and MB trip alarm | General information and announcements to user / Alarm action
60037112 | Any AVR trip alarm | General information and announcements to user / Alarm action
60037113 | Any GB + AVR alarm | General information and announcements to user / Alarm action
60037114 | Any SGB + AVR alarm | General information and announcements to user / Alarm action
60037115 | Any GB + AVR + stop engine alarm | General information and announcements to user / Alarm action
60037116 | Any GB + AVR + shutdown engine alarm | General information and announcements to user / Alarm action
60037117 | Any breaker trip alarm | General information and announcements to user / Alarm action
60037118 | Any breaker trip and stop inverter alarm | General information and announcements to user / Alarm action
60037119 | Any breaker + AVR alarm | General information and announcements to user / Alarm action
60037120 | Any breaker + AVR + stop inverter alarm | General information and announcements to user / Alarm action
60037121 | Any stop inverter alarm | General information and announcements to user / Alarm action
60037122 | Any controlled stop alarm | General information and announcements to user / Alarm action
60050000 | System not OK | General information and announcements to user / Alarm text (pop-ups and logs)
60050010 | System not OK | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60060000 | Enable | General information and announcements to user / Parameter name
60060010 | CustomLogic configuration invalid | General information and announcements to user / Parameter name
60065000 | Is enabled | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60070000 | Configuration update delayed | General information and announcements to user / Alarm text (pop-ups and logs)
60070010 | Critical process error | General information and announcements to user / Alarm text (pop-ups and logs)
60070020 | Restore error | General information and announcements to user / Alarm text (pop-ups and logs)
60070030 | SD-card format error | General information and announcements to user / Alarm text (pop-ups and logs)
60070040 | Communication settings changed (IP address or port configuration). The controller rack must be powered off and on for changes to take effect | General information and announcements to user / Alarm text (pop-ups and logs)
60070050 | Fieldbus configuration exceeded maximum I/O configuration | General information and announcements to user / Alarm text (pop-ups and logs)
60070060 | Cold junction compensation not configured | General information and announcements to user / Alarm text (pop-ups and logs)
60100000 | Signal %s | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60101000 | Enable %s | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60101001 | Integer %s | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60101002 | Float %s | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110000 | UTC year | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110001 | UTC month | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110002 | UTC day | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110003 | UTC hour | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110004 | UTC minute | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110005 | UTC second | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110006 | Local time year | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110007 | Local time month | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110008 | Local time day | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110009 | Local time hour | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110010 | Local time minute | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60110011 | Local time second | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60120000 | Ready | General information and announcements to user / Real-time user interaction (mainly emulation)
60120001 | Not in switchboard control | General information and announcements to user / Real-time user interaction (mainly emulation)
60120002 | Breaker is not open | General information and announcements to user / Real-time user interaction (mainly emulation)
60120003 | Engine is not stopped | General information and announcements to user / Real-time user interaction (mainly emulation)
60120004 | Must leave quick-connect plant | General information and announcements to user / Real-time user interaction (mainly emulation)
60120005 | Inverter is not stopped | General information and announcements to user / Real-time user interaction (mainly emulation)
60120006 | Not in switchboard control or in local | General information and announcements to user / Real-time user interaction (mainly emulation)
60150000 | Custom counter %s | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60165000 | Any high severity alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60165001 | Any medium severity alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60165002 | Any low severity alarm | General information and announcements to user / Assignable function (input/output config menus, Modbus)
60167000 | High | General information and announcements to user / Miscellaneous text (various uses)
60167001 | Medium | General information and announcements to user / Miscellaneous text (various uses)
60167002 | Low | General information and announcements to user / Miscellaneous text (various uses)
70000000 | Period time | Texts regarding regulator configuration and status / Parameter name
70000010 | Minimum ON time | Texts regarding regulator configuration and status / Parameter name
70000020 | Period time | Texts regarding regulator configuration and status / Parameter name
70000030 | Minimum ON time | Texts regarding regulator configuration and status / Parameter name
70000040 | Kp | Texts regarding regulator configuration and status / Parameter name
70000050 | Ti | Texts regarding regulator configuration and status / Parameter name
70000060 | Td | Texts regarding regulator configuration and status / Parameter name
70000070 | Kp | Texts regarding regulator configuration and status / Parameter name
70000080 | Ti | Texts regarding regulator configuration and status / Parameter name
70000090 | Td | Texts regarding regulator configuration and status / Parameter name
70000100 | Kp | Texts regarding regulator configuration and status / Parameter name
70000110 | Ti | Texts regarding regulator configuration and status / Parameter name
70000120 | Td | Texts regarding regulator configuration and status / Parameter name
70000130 | Kp | Texts regarding regulator configuration and status / Parameter name
70000140 | Ti | Texts regarding regulator configuration and status / Parameter name
70000150 | Td | Texts regarding regulator configuration and status / Parameter name
70000160 | P weight | Texts regarding regulator configuration and status / Parameter name
70000170 | Q weight | Texts regarding regulator configuration and status / Parameter name
70000180 | Kp | Texts regarding regulator configuration and status / Parameter name
70000190 | Ti | Texts regarding regulator configuration and status / Parameter name
70000200 | Td | Texts regarding regulator configuration and status / Parameter name
70000210 | Kp | Texts regarding regulator configuration and status / Parameter name
70000220 | Kp | Texts regarding regulator configuration and status / Parameter name
70000230 | Kp | Texts regarding regulator configuration and status / Parameter name
70000240 | Deadband | Texts regarding regulator configuration and status / Parameter name
70000250 | Kp | Texts regarding regulator configuration and status / Parameter name
70000260 | Deadband | Texts regarding regulator configuration and status / Parameter name
70000270 | Kp | Texts regarding regulator configuration and status / Parameter name
70000280 | f deadband | Texts regarding regulator configuration and status / Parameter name
70000290 | P deadband | Texts regarding regulator configuration and status / Parameter name
70000300 | P weight | Texts regarding regulator configuration and status / Parameter name
70000310 | Q weight | Texts regarding regulator configuration and status / Parameter name
70000320 | Kp | Texts regarding regulator configuration and status / Parameter name
70000330 | Ti | Texts regarding regulator configuration and status / Parameter name
70000340 | Td | Texts regarding regulator configuration and status / Parameter name
70000350 | Kp | Texts regarding regulator configuration and status / Parameter name
70000360 | Ti | Texts regarding regulator configuration and status / Parameter name
70000370 | Td | Texts regarding regulator configuration and status / Parameter name
70000380 | Kp | Texts regarding regulator configuration and status / Parameter name
70000390 | Ti | Texts regarding regulator configuration and status / Parameter name
70000400 | Td | Texts regarding regulator configuration and status / Parameter name
70000410 | Kp | Texts regarding regulator configuration and status / Parameter name
70000420 | Deadband | Texts regarding regulator configuration and status / Parameter name
70000430 | Kp | Texts regarding regulator configuration and status / Parameter name
70000440 | V deadband | Texts regarding regulator configuration and status / Parameter name
70000450 | Kp | Texts regarding regulator configuration and status / Parameter name
70000460 | Deadband | Texts regarding regulator configuration and status / Parameter name
70000470 | Q deadband | Texts regarding regulator configuration and status / Parameter name
70000480 | Manual AVR slope | Texts regarding regulator configuration and status / Parameter name
70000490 | Manual GOV slope | Texts regarding regulator configuration and status / Parameter name
70000500 | Base load | Texts regarding regulator configuration and status / Parameter name
70000510 | Set point | Texts regarding regulator configuration and status / Parameter name
70000520 | GOV regulation error | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000530 | AVR regulation error | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000540 | Minimum ON time test | Texts regarding regulator configuration and status / Parameter name
70000550 | Minimum ON time test | Texts regarding regulator configuration and status / Parameter name
70000560 | Regulator delay | Texts regarding regulator configuration and status / Timer text
70000570 | Maximum load sharing | Texts regarding regulator configuration and status / Parameter name
70000580 | Load sharing type | Texts regarding regulator configuration and status / Parameter name
70000590 | P load sharing failure | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000600 | Q load sharing failure | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000710 | AVR relay setup incomplete | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000720 | GOV relay setup incomplete | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000750 | AVR output selection failure | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000760 | GOV output selection failure | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000770 | Output type | Texts regarding regulator configuration and status / Parameter name
70000780 | Output type | Texts regarding regulator configuration and status / Parameter name
70000790 | Frequency offset source | Texts regarding regulator configuration and status / Parameter name
70000800 | Frequency offset enable | Texts regarding regulator configuration and status / Parameter name
70000810 | P set point source | Texts regarding regulator configuration and status / Parameter name
70000820 | P set point enable | Texts regarding regulator configuration and status / Parameter name
70000830 | Q set point source | Texts regarding regulator configuration and status / Parameter name
70000840 | Q set point enable | Texts regarding regulator configuration and status / Parameter name
70000850 | Voltage offset source | Texts regarding regulator configuration and status / Parameter name
70000860 | Voltage offset enable | Texts regarding regulator configuration and status / Parameter name
70000870 | Cos phi set point source | Texts regarding regulator configuration and status / Parameter name
70000880 | Cos phi set point enable | Texts regarding regulator configuration and status / Parameter name
70000890 | Set point | Texts regarding regulator configuration and status / Parameter name
70000900 | Set point | Texts regarding regulator configuration and status / Parameter name
70000910 | GOV regulator mode not selected | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000920 | AVR regulator mode not selected | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000930 | Multiple GOV regulator modes selected | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000940 | Multiple AVR regulator modes selected | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70000950 | Maximum ON time | Texts regarding regulator configuration and status / Parameter name
70000960 | Maximum ON time | Texts regarding regulator configuration and status / Parameter name
70000970 | Set point adjustment | Texts regarding regulator configuration and status / Parameter name
70000980 | Set point adjustment | Texts regarding regulator configuration and status / Parameter name
70000990 | Set point | Texts regarding regulator configuration and status / Parameter name
70001000 | Set point | Texts regarding regulator configuration and status / Parameter name
70001010 | Regulator delay | Texts regarding regulator configuration and status / Timer text
70001020 | Ramping method | Texts regarding regulator configuration and status / Parameter name
70001030 | Ramping method | Texts regarding regulator configuration and status / Parameter name
70001040 | Cos phi reset point | Texts regarding regulator configuration and status / Parameter name
70001050 | Offset 1 | Texts regarding regulator configuration and status / Parameter name
70001060 | Offset 2 | Texts regarding regulator configuration and status / Parameter name
70001070 | Offset 3 | Texts regarding regulator configuration and status / Parameter name
70001080 | Offset 1 | Texts regarding regulator configuration and status / Parameter name
70001090 | Offset 1 | Texts regarding regulator configuration and status / Parameter name
70001100 | Offset 2 | Texts regarding regulator configuration and status / Parameter name
70001110 | Offset 2 | Texts regarding regulator configuration and status / Parameter name
70001120 | Offset 3 | Texts regarding regulator configuration and status / Parameter name
70001130 | Offset 3 | Texts regarding regulator configuration and status / Parameter name
70001140 | Offset 1 | Texts regarding regulator configuration and status / Parameter name
70001150 | Offset 1 | Texts regarding regulator configuration and status / Parameter name
70001160 | Offset 2 | Texts regarding regulator configuration and status / Parameter name
70001170 | Offset 2 | Texts regarding regulator configuration and status / Parameter name
70001180 | Offset 3 | Texts regarding regulator configuration and status / Parameter name
70001190 | Offset 3 | Texts regarding regulator configuration and status / Parameter name
70001200 | Kp | Texts regarding regulator configuration and status / Parameter name
70001210 | Ti | Texts regarding regulator configuration and status / Parameter name
70001220 | Td | Texts regarding regulator configuration and status / Parameter name
70001230 | Kp | Texts regarding regulator configuration and status / Parameter name
70001240 | Ramp selection | Texts regarding regulator configuration and status / Parameter name
70001250 | Kp | Texts regarding regulator configuration and status / Parameter name
70001260 | Ti | Texts regarding regulator configuration and status / Parameter name
70001270 | Td | Texts regarding regulator configuration and status / Parameter name
70001280 | Kp | Texts regarding regulator configuration and status / Parameter name
70001290 | Deadband | Texts regarding regulator configuration and status / Parameter name
70001300 | Kp | Texts regarding regulator configuration and status / Parameter name
70001310 | Ti | Texts regarding regulator configuration and status / Parameter name
70001320 | Td | Texts regarding regulator configuration and status / Parameter name
70001330 | Kp | Texts regarding regulator configuration and status / Parameter name
70001340 | Ti | Texts regarding regulator configuration and status / Parameter name
70001350 | Td | Texts regarding regulator configuration and status / Parameter name
70001360 | Period time | Texts regarding regulator configuration and status / Parameter name
70001370 | Minimum ON time | Texts regarding regulator configuration and status / Parameter name
70001380 | Maximum ON time | Texts regarding regulator configuration and status / Parameter name
70001390 | Period time | Texts regarding regulator configuration and status / Parameter name
70001400 | Minimum ON time | Texts regarding regulator configuration and status / Parameter name
70001410 | Maximum ON time | Texts regarding regulator configuration and status / Parameter name
70001420 | Limit 1 | Texts regarding regulator configuration and status / Parameter name
70001430 | Limit 1 | Texts regarding regulator configuration and status / Parameter name
70001440 | Limit 2 | Texts regarding regulator configuration and status / Parameter name
70001450 | Limit 2 | Texts regarding regulator configuration and status / Parameter name
70001460 | Limit 1 | Texts regarding regulator configuration and status / Parameter name
70001470 | Limit 2 | Texts regarding regulator configuration and status / Parameter name
70001480 | Limit 1 | Texts regarding regulator configuration and status / Parameter name
70001490 | Limit 2 | Texts regarding regulator configuration and status / Parameter name
70001500 | Mains parallel | Texts regarding regulator configuration and status / Parameter name
70001510 | Selection | Texts regarding regulator configuration and status / Parameter name
70001520 | Selection | Texts regarding regulator configuration and status / Parameter name
70001530 | Set point unit | Texts regarding regulator configuration and status / Parameter name
70001540 | Set point | Texts regarding regulator configuration and status / Parameter name
70001550 | Load share | Texts regarding regulator configuration and status / Parameter name
70001560 | Fixed frequency | Texts regarding regulator configuration and status / Parameter name
70100000 | AVR output | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100001 | GOV output | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100002 | AVR increase | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100003 | AVR decrease | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100004 | GOV increase | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100005 | GOV decrease | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100006 | P load sharing input | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100007 | P load sharing output | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100008 | Q load sharing input | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100009 | Q load sharing output | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100010 | GOV regulator mode not selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100011 | AVR regulator mode not selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100012 | AVR relay setup incomplete | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100013 | GOV relay setup incomplete | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100014 | AVR output setup failure | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100015 | GOV output setup failure | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100016 | AVR output selection failure | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100017 | GOV output selection failure | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100018 | GOV regulator error | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100019 | AVR regulator error | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100020 | P load sharing failure | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100021 | Q load sharing failure | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100022 | GOV regulator | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100023 | GOV regulator error | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100024 | GOV regulator reference | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100025 | GOV regulator actual value | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100026 | GOV regulator type | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100027 | AVR regulator | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100028 | AVR regulator error | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100029 | AVR regulator reference | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100030 | AVR regulator actual value | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100031 | AVR regulator type | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100032 | AVR regulator percentage | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100033 | GOV regulator percentage | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100034 | Frequency offset | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100035 | Power set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100036 | Voltage offset | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100037 | Reactive power set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100038 | Cos phi set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100039 | Activate external V offset | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100040 | Deactivate external V offset | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100041 | Activate external Q set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100042 | Deactivate external Q set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100043 | Activate external cos phi set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100044 | Deactivate external cos phi set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100045 | Activate external f offset | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100046 | Deactivate external f offset | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100047 | Activate external P set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100048 | Deactivate external P set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100049 | Multiple GOV regulator modes selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100050 | Multiple AVR regulator modes selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100051 | Regulation ON | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100052 | Freeze regulator | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100053 | Pause ramping | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100054 | Pause ramping | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100055 | Deactivate regulation | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100056 | Deactivate regulation | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100057 | Active power offset 1 | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100058 | Active power offset 2 | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100059 | Active power offset 3 | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100060 | Cos phi/Reactive power offset 1 | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100061 | Cos phi/Reactive power offset 2 | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100062 | Cos phi/Reactive power offset 3 | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100063 | Activate ramp 1 | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100064 | Activate ramp 2 | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100065 | Override GOV automatic regulator mode | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100066 | Override AVR automatic regulator mode | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100067 | Cos phi reference | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100200 | Activate fixed frequency | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100201 | Activate fixed power | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100202 | Activate frequency droop | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100203 | Activate power load sharing | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100204 | Activate external set point (network) | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100205 | Activate external set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100206 | Activate external set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100207 | Activate manual regulation | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100208 | Activate fixed RPM | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100210 | Deactivate fixed frequency | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100211 | Deactivate fixed power | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100212 | Deactivate frequency droop | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100213 | Deactivate power load sharing | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100214 | Deactivate external set point (network) | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100215 | Deactivate external set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100216 | Deactivate external set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100217 | Deactivate manual regulation | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100220 | Fixed frequency regulation is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100221 | Fixed power regulation is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100222 | Frequency droop regulation is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100223 | Power load sharing is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100224 | Manual GOV regulation is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100225 | External set point (network) is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100226 | External set point is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100227 | External set point is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100228 | Fixed RPM is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100230 | Fixed frequency regulation is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100231 | Fixed power regulation is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100232 | Frequency droop regulation is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100233 | Power load sharing is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100235 | External set point (network) is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100236 | External set point is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100237 | External set point is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100238 | GOV manual regulation is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100500 | Activate fixed voltage | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100501 | Activate fixed reactive power | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100502 | Activate fixed cos phi | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100503 | Activate voltage droop | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100504 | Activate reactive power load sharing | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100505 | Activate external set point (network) | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100506 | Activate external set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100507 | Activate external set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100508 | Activate manual regulation | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100510 | Deactivate fixed voltage | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100511 | Deactivate fixed reactive power | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100512 | Deactivate fixed cos phi | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100513 | Deactivate voltage droop | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100514 | Deactivate reactive power load sharing | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100515 | Deactivate external set point (network) | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100516 | Deactivate external set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100517 | Deactivate external set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100518 | Deactivate manual regulation | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100520 | Fixed voltage is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100521 | Fixed reactive power is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100522 | Fixed cos phi is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100523 | Reactive power load sharing is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100524 | Voltage droop is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100525 | Manual AVR regulation is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100526 | External set point (network) is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100527 | External set point is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100528 | External set point is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100530 | Fixed voltage is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100531 | Fixed reactive power is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100532 | Fixed cos phi is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100533 | Reactive power load sharing is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100534 | Voltage droop is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100536 | External set point (network) is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100537 | External set point is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100538 | External set point is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100539 | AVR manual regulation is selected | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100540 | Selected GOV regulation mode | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100541 | Active GOV regulation mode | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100542 | GOV set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100543 | GOV measured value | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100544 | GOV regulation source | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100545 | GOV external regulation source value | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100546 | GOV regulation manual input | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100560 | Selected AVR regulation mode | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100561 | Active AVR regulation mode | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100562 | AVR set point | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100563 | AVR measured value | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100564 | AVR regulation source | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100565 | AVR external regulation source value | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70100566 | AVR regulation manual input | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
70200000 | Power ramp up speed | Texts regarding regulator configuration and status / Parameter name
70200010 | Power ramp up error | Texts regarding regulator configuration and status / Parameter name
70200020 | Power ramp down speed | Texts regarding regulator configuration and status / Parameter name
70200030 | Power ramp down error | Texts regarding regulator configuration and status / Parameter name
70200040 | Warm up set point | Texts regarding regulator configuration and status / Parameter name
70200050 | Steps | Texts regarding regulator configuration and status / Parameter name
70200060 | Island ramping | Texts regarding regulator configuration and status / Parameter name
70200070 | Speed | Texts regarding regulator configuration and status / Parameter name
70200080 | Speed | Texts regarding regulator configuration and status / Parameter name
70200090 | Enable ramping | Texts regarding regulator configuration and status / Parameter name
70200100 | Enter operation ramp enable | Texts regarding regulator configuration and status / Parameter name
70200110 | Deload ramp enable | Texts regarding regulator configuration and status / Parameter name
70200300 | Ramp 1 | Texts regarding regulator configuration and status / Parameter name
70200400 | Ramp 1 | Texts regarding regulator configuration and status / Parameter name
70200500 | Ramp 2 | Texts regarding regulator configuration and status / Parameter name
70200600 | Ramp 2 | Texts regarding regulator configuration and status / Parameter name
70200700 | Ramp 1 | Texts regarding regulator configuration and status / Parameter name
70200800 | Ramp 1 | Texts regarding regulator configuration and status / Parameter name
70200900 | Operation ramp up | Texts regarding regulator configuration and status / Parameter name
70201000 | Operation ramp down | Texts regarding regulator configuration and status / Parameter name
70201100 | Enter operation ramp | Texts regarding regulator configuration and status / Parameter name
70201200 | Deload ramp | Texts regarding regulator configuration and status / Parameter name
70201300 | Operation ramp up | Texts regarding regulator configuration and status / Parameter name
70201400 | Operation ramp down | Texts regarding regulator configuration and status / Parameter name
70350000 | Power ramp up error | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70350001 | Power ramp down error | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70350002 | Enter operation ramp active | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70350003 | Operation ramp active | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70350004 | Deload ramp active | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
70400000 | Off | Texts regarding regulator configuration and status / Status text (info lines)
70400001 | Relay | Texts regarding regulator configuration and status / Status text (info lines)
70400002 | Analogue | Texts regarding regulator configuration and status / Status text (info lines)
70400003 | Engine interface communication | Texts regarding regulator configuration and status / Status text (info lines)
70400004 | Hardware select | Texts regarding regulator configuration and status / Status text (info lines)
70400005 | Inductive | Texts regarding regulator configuration and status / Status text (info lines)
70400006 | Capacitive | Texts regarding regulator configuration and status / Status text (info lines)
70400007 | Synchronise and close breaker | Texts regarding regulator configuration and status / Status text (info lines)
70400008 | Sync check (signal when in sync.) | Texts regarding regulator configuration and status / Status text (info lines)
70400009 | Infinite synchronisation (no breaker operation) | Texts regarding regulator configuration and status / Status text (info lines)
70400010 | Frequency regulation | Texts regarding regulator configuration and status / Status text (info lines)
70400011 | Synchronising GB | Texts regarding regulator configuration and status / Status text (info lines)
70400012 | Synchronising TB | Texts regarding regulator configuration and status / Status text (info lines)
70400013 | Load sharing | Texts regarding regulator configuration and status / Status text (info lines)
70400014 | Load sharing (asymmetric) | Texts regarding regulator configuration and status / Status text (info lines)
70400015 | Ramping up/down | Texts regarding regulator configuration and status / Status text (info lines)
70400016 | Fixed power | Texts regarding regulator configuration and status / Status text (info lines)
70400017 | Synchronising ext. breaker | Texts regarding regulator configuration and status / Status text (info lines)
70400018 | De-loading ext. breaker | Texts regarding regulator configuration and status / Status text (info lines)
70400019 | Manual regulation | Texts regarding regulator configuration and status / Status text (info lines)
70400023 | Voltage regulation | Texts regarding regulator configuration and status / Status text (info lines)
70400024 | Fixed reactive power | Texts regarding regulator configuration and status / Status text (info lines)
70400025 | Fixed cos phi | Texts regarding regulator configuration and status / Status text (info lines)
70400026 | Frequency droop regulation | Texts regarding regulator configuration and status / Status text (info lines)
70400027 | Voltage droop regulation | Texts regarding regulator configuration and status / Status text (info lines)
70400028 | Ramping to | Texts regarding regulator configuration and status / Status text (info lines)
70400029 | Reactive power curve | Texts regarding regulator configuration and status / Status text (info lines)
70400030 | Fixed cos phi | Texts regarding regulator configuration and status / Status text (info lines)
70400031 | Ramping paused | Texts regarding regulator configuration and status / Status text (info lines)
70400032 | Reactive power | Texts regarding regulator configuration and status / Status text (info lines)
70400033 | Analogue / ECU | Texts regarding regulator configuration and status / Status text (info lines)
70400034 | Frequency deviation | Texts regarding regulator configuration and status / Status text (info lines)
70400035 | Voltage deviation | Texts regarding regulator configuration and status / Status text (info lines)
70400036 | Active power | Texts regarding regulator configuration and status / Status text (info lines)
70400037 | Reactive power offset | Texts regarding regulator configuration and status / Status text (info lines)
70400038 | Cos phi offset | Texts regarding regulator configuration and status / Status text (info lines)
70400039 | RPM regulation | Texts regarding regulator configuration and status / Status text (info lines)
70400040 | Preferred | Texts regarding regulator configuration and status / Status text (info lines)
70400041 | Locked | Texts regarding regulator configuration and status / Status text (info lines)
70400042 | No regulation | Texts regarding regulator configuration and status / Status text (info lines)
70400043 | Frequency synchronisation | Texts regarding regulator configuration and status / Status text (info lines)
70400044 | Phase synchronisation | Texts regarding regulator configuration and status / Status text (info lines)
70400045 | Reactive power snapshot | Texts regarding regulator configuration and status / Status text (info lines)
70400046 | Nominal reactive power | Texts regarding regulator configuration and status / Status text (info lines)
70400047 | Regulator frozen | Texts regarding regulator configuration and status / Status text (info lines)
70400048 | I | Texts regarding regulator configuration and status / Status text (info lines)
70400049 | C | Texts regarding regulator configuration and status / Status text (info lines)
70400050 | GOV status | Texts regarding regulator configuration and status / Status text (info lines)
70400051 | GOV selected regulation mode | Texts regarding regulator configuration and status / Status text (info lines)
70400052 | GOV active regulation mode | Texts regarding regulator configuration and status / Status text (info lines)
70400053 | GOV set point | Texts regarding regulator configuration and status / Status text (info lines)
70400054 | GOV actual value | Texts regarding regulator configuration and status / Status text (info lines)
70400055 | GOV actual output | Texts regarding regulator configuration and status / Status text (info lines)
70400056 | GOV regulator not configured | Texts regarding regulator configuration and status / Status text (info lines)
70400057 | GOV regulator source | Texts regarding regulator configuration and status / Status text (info lines)
70400058 | GOV regulator external offset | Texts regarding regulator configuration and status / Status text (info lines)
70400059 | GOV regulator manual input | Texts regarding regulator configuration and status / Status text (info lines)
70400060 | AVR status | Texts regarding regulator configuration and status / Status text (info lines)
70400061 | AVR selected regulation mode | Texts regarding regulator configuration and status / Status text (info lines)
70400062 | AVR active regulation mode | Texts regarding regulator configuration and status / Status text (info lines)
70400063 | AVR set point | Texts regarding regulator configuration and status / Status text (info lines)
70400064 | AVR actual value | Texts regarding regulator configuration and status / Status text (info lines)
70400065 | AVR actual output | Texts regarding regulator configuration and status / Status text (info lines)
70400066 | AVR regulator not configured | Texts regarding regulator configuration and status / Status text (info lines)
70400067 | AVR regulator source | Texts regarding regulator configuration and status / Status text (info lines)
70400068 | AVR regulator external offset | Texts regarding regulator configuration and status / Status text (info lines)
70400069 | AVR regulator manual input | Texts regarding regulator configuration and status / Status text (info lines)
70400070 | Manual | Texts regarding regulator configuration and status / Status text (info lines)
70400071 | Automatic | Texts regarding regulator configuration and status / Status text (info lines)
70400072 | In percent | Texts regarding regulator configuration and status / Status text (info lines)
70400073 | In kW | Texts regarding regulator configuration and status / Status text (info lines)
70400074 | Active power snapshot | Texts regarding regulator configuration and status / Status text (info lines)
70400075 | Nominal power | Texts regarding regulator configuration and status / Status text (info lines)
70400080 | External Modbus | Texts regarding regulator configuration and status / Status text (info lines)
70400081 | External analogue | Texts regarding regulator configuration and status / Status text (info lines)
70400082 | CustomLogic | Texts regarding regulator configuration and status / Status text (info lines)
70400083 | CODESYS | Texts regarding regulator configuration and status / Status text (info lines)
70400084 | DEIF network | Texts regarding regulator configuration and status / Status text (info lines)
70400085 | Nominal | Texts regarding regulator configuration and status / Status text (info lines)
70400086 | Synchronising | Texts regarding regulator configuration and status / Status text (info lines)
70400087 | Relay | Texts regarding regulator configuration and status / Status text (info lines)
70400088 | No source | Texts regarding regulator configuration and status / Status text (info lines)
70400089 | Unknown | Texts regarding regulator configuration and status / Status text (info lines)
70400090 | Up is active | Texts regarding regulator configuration and status / Status text (info lines)
70400091 | Down is active | Texts regarding regulator configuration and status / Status text (info lines)
70400092 | Not active | Texts regarding regulator configuration and status / Status text (info lines)
70400093 | External Digital | Texts regarding regulator configuration and status / Status text (info lines)
70400094 | Warm up | Texts regarding regulator configuration and status / Status text (info lines)
70400095 | Ramp frozen | Texts regarding regulator configuration and status / Status text (info lines)
70400096 | Analogue / Digital AVR | Texts regarding regulator configuration and status / Status text (info lines)
70451000 | Droop curve | Texts regarding regulator configuration and status / Graph text (heading or axis name)
70451300 | Droop enable | Texts regarding regulator configuration and status / Parameter name
70451310 | Hysteresis low limit | Texts regarding regulator configuration and status / Parameter name
70451320 | Hysteresis low enable | Texts regarding regulator configuration and status / Parameter name
70451330 | Hysteresis high limit | Texts regarding regulator configuration and status / Parameter name
70451340 | Hysteresis high enable | Texts regarding regulator configuration and status / Parameter name
70451350 | Frequency-dependent power droop started | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70451360 | Frequency-dependent power droop stopped | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70451370 | Offset calculated from | Texts regarding regulator configuration and status / Parameter name
70452000 | Droop curve | Texts regarding regulator configuration and status / Graph text (heading or axis name)
70452300 | Droop enable | Texts regarding regulator configuration and status / Parameter name
70452310 | Hysteresis low limit | Texts regarding regulator configuration and status / Parameter name
70452320 | Hysteresis low enable | Texts regarding regulator configuration and status / Parameter name
70452330 | Hysteresis high limit | Texts regarding regulator configuration and status / Parameter name
70452340 | Hysteresis high enable | Texts regarding regulator configuration and status / Parameter name
70452350 | Voltage-dependent reactive power droop started | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70452360 | Voltage-dependent reactive power droop stopped | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70452370 | Offset calculated from | Texts regarding regulator configuration and status / Parameter name
70453000 | Droop curve | Texts regarding regulator configuration and status / Graph text (heading or axis name)
70453300 | Droop enable | Texts regarding regulator configuration and status / Parameter name
70453310 | Hysteresis low limit | Texts regarding regulator configuration and status / Parameter name
70453320 | Hysteresis low enable | Texts regarding regulator configuration and status / Parameter name
70453330 | Hysteresis high limit | Texts regarding regulator configuration and status / Parameter name
70453340 | Hysteresis high enable | Texts regarding regulator configuration and status / Parameter name
70453350 | Voltage-dependent cos phi droop started | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70453360 | Voltage-dependent cos phi droop stopped | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70454000 | Droop curve | Texts regarding regulator configuration and status / Graph text (heading or axis name)
70454300 | Droop enable | Texts regarding regulator configuration and status / Parameter name
70454310 | Power-dependent cos phi droop started | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70454320 | Power-dependent cos phi droop stopped | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70455000 | Droop curve | Texts regarding regulator configuration and status / Graph text (heading or axis name)
70455300 | Droop enable | Texts regarding regulator configuration and status / Parameter name
70455310 | Power-dependent cos phi droop started | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
70455320 | Power-dependent cos phi droop stopped | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
80000020 | GOV stand-alone configuration error | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
80000030 | AVR stand-alone configuration error | Texts regarding regulator configuration and status / Alarm text (pop-ups and logs)
80000040 | GOV stand-alone activation | Texts regarding regulator configuration and status / Parameter name
80000050 | AVR stand-alone activation | Texts regarding regulator configuration and status / Parameter name
80050000 | High | Texts regarding regulator configuration and status / Parameter configuration (selected from a list)
80050001 | Low | Texts regarding regulator configuration and status / Parameter configuration (selected from a list)
80100000 | Stand-alone mode | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
80100001 | Stand-alone mode | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
80100002 | Stand-alone is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
80100003 | Stand-alone is active | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
80100004 | GOV stand-alone configuration error | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
80100005 | AVR stand-alone configuration error | Texts regarding regulator configuration and status / Assignable function (input/output config menus, Modbus)
81000000 | Module update required | Texts regarding regulator configuration and status / Status text (info lines)
81000001 | Press Update for update and reboot | Texts regarding regulator configuration and status / Status text (info lines)
81000002 | Module update not possible | Texts regarding regulator configuration and status / Status text (info lines)
81000003 | Update | Texts regarding regulator configuration and status / Status text (info lines)
81000004 | Postpone | Texts regarding regulator configuration and status / Status text (info lines)
81000005 | The update will take several minutes | Texts regarding regulator configuration and status / Status text (info lines)
81100000 | Module firmware update | Texts regarding regulator configuration and status / Event text (pop-ups, logs and status texts)
82000000 | Currently | Texts regarding CPU monitoring / Assignable function (input/output config menus, Modbus)
82000010 | Average over 10 seconds | Texts regarding CPU monitoring / Assignable function (input/output config menus, Modbus)
82000020 | Average over 1 minute | Texts regarding CPU monitoring / Assignable function (input/output config menus, Modbus)
82000030 | Average over 10 minutes | Texts regarding CPU monitoring / Assignable function (input/output config menus, Modbus)
90000000 | Required IO card(s) not found | Texts related to controller operations / Alarm text (pop-ups and logs)
90000010 | Software mismatch on hardware module(s) | Texts related to controller operations / Alarm text (pop-ups and logs)
90000020 | Controller type mismatch | Texts related to controller operations / Alarm text (pop-ups and logs)
90000030 | Forced to switchboard control | Texts related to controller operations / Alarm text (pop-ups and logs)
90010000 | Required HW and IO card SW found | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90020000 | Switchboard control | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90020001 | Required IO card(s) not found | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90020002 | Incompatible SW on IO card(s) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90020003 | Controller type mismatch | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90020004 | Forced to switchboard control | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90020005 | Under switchboard control | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90020007 | PMS control | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90020008 | Normal operation | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90040000 | Alarm blocking engine start | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040001 | Alarm blocking GB close | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040002 | Alarm blocking BTB close | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040003 | Alarm blocking SGB close | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040004 | Alarm blocking TB close | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040005 | Alarm blocking SCB close | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040006 | Alarm blocking MB close | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040007 | Alarm blocking start | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040008 | Alarm blocking breaker close | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040012 | Phase sequence error both sides | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90040018 | Verifying SC removed | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90100000 | Forced to MANUAL | Texts related to controller operations / Alarm text (pop-ups and logs)
90100010 | Mode | Texts related to controller operations / Parameter name
90100020 | Mode | Texts related to controller operations / Parameter name
90100030 | Terminal A L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90100040 | Terminal B L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90100050 | Terminal A L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90100060 | Terminal A L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90100070 | Terminal A L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90100080 | Terminal B L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90100090 | Terminal B L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90100100 | Terminal B L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90100110 | GAM3.2 1 status not OK | Texts related to controller operations / Alarm text (pop-ups and logs)
90100120 | GAM3.2 2 status not OK | Texts related to controller operations / Alarm text (pop-ups and logs)
90100130 | GAM3.2 3 status not OK | Texts related to controller operations / Alarm text (pop-ups and logs)
90100140 | Generator type | Texts related to controller operations / Parameter name
90100150 | Synchronous | Texts related to controller operations / Miscellaneous text (various uses)
90100160 | Asynchronous | Texts related to controller operations / Miscellaneous text (various uses)
90100170 | Delta speed min. | Texts related to controller operations / Parameter name
90100180 | No synchronisation signal for asynchronous generator | Texts related to controller operations / Alarm text (pop-ups and logs)
90100190 | Asynchronous generator over-voltage | Texts related to controller operations / Alarm text (pop-ups and logs)
90100200 | Delta speed max. | Texts related to controller operations / Parameter name
90100210 | Return mode | Texts related to controller operations / Parameter name
90100260 | Test | Texts related to controller operations / Parameter name
90100270 | Test type | Texts related to controller operations / Parameter name
90100280 | Return mode | Texts related to controller operations / Parameter name
90100300 | TB de-load before GB | Texts related to controller operations / Parameter name
90110000 | Mode changed to AUTO | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110010 | Mode changed to MANUAL | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110020 | Secured mode activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110030 | Secured mode deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110040 | Load-dependent stop block activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110050 | Load-dependent stop block deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110060 | Force all in section to SWBD control activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110070 | Force all in section to SWBD control deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110080 | Force all in section to MANUAL activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110090 | Force all in section to AUTO activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110100 | Precautionary genset start activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110110 | Precautionary genset start deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110120 | Blackout start block activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110130 | Blackout start block deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110140 | Acknowledge all alarms in system | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110150 | Control changed to local | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110160 | Control changed to remote | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110170 | Static synchronisation activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110180 | Static synchronisation deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110190 | Dynamic synchronisation activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110200 | Dynamic synchronisation deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110210 | Static MB synchronisation activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110220 | Static MB synchronisation deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110230 | Dynamic MB synchronisation activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110240 | Dynamic MB synchronisation deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110250 | Power management | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110260 | Peak shaving | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110270 | Fixed power | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110280 | Mains power export | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110290 | Load take over | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110300 | Test mode | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110310 | Total test on | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110320 | Total test off | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110330 | Auto mains failure | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110340 | Alternative start on | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110350 | Alternative start off | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110360 | Auto start stop on | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110370 | Auto start stop off | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110380 | Block mode | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110390 | Island operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90110400 | Test DAVR mode | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90120000 | Forced to MANUAL | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120009 | GAM3.2 1 status OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120010 | GAM3.2 2 status OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120011 | GAM3.2 3 status OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120012 | GAM3.2 1 status OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120013 | GAM3.2 2 status OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120014 | GAM3.2 3 status OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120015 | GAM3.2 1 status not OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120016 | GAM3.2 2 status not OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120017 | GAM3.2 3 status not OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90120018 | Trip AVR | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130000 | Start engine | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130001 | Stop engine | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130002 | Block engine start | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130003 | Block blackout start | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130004 | Acknowledge all alarms in system | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130005 | Block load-dependent stop | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130006 | Deactivate secured mode | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130007 | Activate secured mode | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130008 | Force analogue load sharing | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130009 | Force all controllers in section to SWBD control | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130010 | Force all gensets in section to MANUAL | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130011 | Force all gensets in section to AUTO | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130015 | Precautionary genset start | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130016 | Unblock load-dependent stop | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130017 | Auto start/stop | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130018 | Start | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90130019 | Stop | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90140000 | Engine start not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140001 | Engine stop not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140002 | Engine block not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140003 | GB open not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140004 | GB close not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140005 | Engine start and breaker close not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140006 | GB open and stop not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140007 | GB block not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140008 | Switchboard control | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140009 | 1st priority not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140010 | GB open without de-loading not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140011 | Change of synchronisation settings not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90140012 | Last priority not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150000 | Not in MANUAL | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150001 | Busbar V/Hz not OK | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150002 | Generator V/Hz not OK | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150003 | Load on busbar too high | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150004 | Available power too low | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150005 | Breaker already closed | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150006 | Already selected | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150007 | Regulation not possible | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150008 | GB open not possible | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150009 | Load-dependent stop blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150010 | Only one connected | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150011 | De-load cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150012 | Synchronisation cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150013 | Breaker already opened | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150014 | Gensets are handling blackout | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150015 | No genset ready to start | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150016 | Maximum gensets exceeded in section | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150017 | Another breaker is closing | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150018 | Are all DGs in AUTO? | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150019 | Any busbar frequency missing | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150020 | Connected DG(s) in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150021 | Secured mode active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150022 | SG (PTH) - SC not possible | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150023 | Blackout start blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150024 | Not under local control | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150025 | Not under remote control | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150026 | Engine not running | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150027 | Any mains frequency missing | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150028 | Display commands are not active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150029 | PICUS commands are not active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150030 | Non-regulating EDG connected | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150031 | Non-regulating SG or SC connected | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150032 | Only one SC connected | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150033 | Load increased while de-loading genset(s). Returning to DG supply | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150034 | Load increased while de-loading genset(s). Continuing to de-load genset(s) | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150035 | The base load cannot be disabled because the section load is too high for the SG | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150036 | The base load cannot be disabled because the section load is too high for the SC | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150037 | Harbour operation active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150039 | Busbar blocked by GB | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150040 | Busbar blocked by TB | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150041 | Busbar blocked by MB | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150042 | Request BTB in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150043 | Dividing section in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150044 | Auto mains failure manual | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150045 | Auto mains failure auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150046 | Auto mains failure no regulation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150047 | Ready auto mains failure auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150048 | Auto mains failure active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150049 | Island auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150050 | Island manual | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150051 | Island no regulation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150052 | Ready island auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150053 | Island active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150054 | Peak shaving manual | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150055 | Peak shaving no regulation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150056 | Peak shaving auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150057 | Ready peak shaving auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150058 | Peak shaving active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150059 | Mains power export manual | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150060 | Mains power export no regulation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150061 | Mains power export auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150062 | Ready mains power export auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150063 | Mains power export active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150064 | Fixed power manual | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150065 | Fixed power no regulation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150066 | Fixed power auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150067 | Ready fixed power auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150068 | Fixed power active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150069 | Load take over manual | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150070 | Load take over auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150071 | Ready load take over auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150072 | Load take over active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150073 | Load take over no regulation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150074 | Dry alternator auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150075 | Dry alternator manual | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150076 | Dry alternator no regulation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150077 | Ready dry alternator auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150078 | Dry alternator active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150079 | Ventilation auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150080 | Ready ventilation auto | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150081 | Ventilation active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150082 | Ventilation manual | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150083 | Ventilation no regulation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150084 | Simple test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150085 | Load test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150086 | Full test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150087 | Awaiting mode info | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150088 | Simple test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150089 | Load test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150090 | Full test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150091 | Select genset mode | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150092 | Select plant mode | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150093 | Unexpected GB on busbar | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150094 | Unexpected TB on busbar | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150116 | Fixed power | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150117 | Auto mains failure | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150118 | Peak shaving | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150119 | Mains power export | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90150120 | Load take over | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90160100 | Retrofit control register 2 PPU-2 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90160101 | Retrofit control register 6 PPU-2 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90160102 | Retrofit control register 5 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90160103 | Retrofit control register 6 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90160104 | Retrofit control register 7 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90160105 | Retrofit control register 8 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90160106 | Retrofit control register 9 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90160107 | Retrofit control register 11 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90160108 | Retrofit control register 12 | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90200000 | Enable | Texts related to controller operations / Parameter name
90200010 | Set point | Texts related to controller operations / Parameter name
90200020 | DG-SG max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90200030 | DG-SC max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90200040 | Delay | Texts related to controller operations / Timer text
90200050 | Source | Texts related to controller operations / Parameter name
90200060 | Source | Texts related to controller operations / Parameter name
90200070 | Enable | Texts related to controller operations / Parameter name
90200080 | Set point | Texts related to controller operations / Parameter name
90200090 | Delay | Texts related to controller operations / Timer text
90200100 | Allow blackout recovery | Texts related to controller operations / Miscellaneous text (various uses)
90200110 | Load too high | Texts related to controller operations / Alarm text (pop-ups and logs)
90200150 | Breaker type | Texts related to controller operations / Parameter name
90210000 | GB close blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90210010 | GB close not blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90210020 | First priority selected | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90210030 | Genset starting - SG f [Hz] | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90210040 | Genset synchronising - SG f [Hz] | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90210050 | Last priority selected | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90210060 | Stop non-connected DG | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90220000 | DG-SG max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90220001 | DG-SC max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90220002 | Is first priority | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90220003 | Is first standby | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90220004 | P set point | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90220005 | Q set point | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90220006 | Mains in parallel | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90220007 | DG-Hybrid max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90220009 | Is second standby | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230000 | GB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230001 | GB open | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230002 | Start engine and close generator breaker | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230003 | Open generator breaker and stop engine | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230004 | Block GB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230005 | 1st priority | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230006 | Manual GOV increase | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230007 | Manual GOV decrease | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230008 | Manual AVR increase | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230009 | Manual AVR decrease | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230010 | Reset AVR to offset | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230011 | Reset GOV to offset | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230012 | Activate asymmetric P load sharing | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230013 | Activate asymmetric Q load sharing | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230014 | Deactivate asymmetric P load sharing | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230015 | Deactivate asymmetric Q load sharing | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230016 | GB open without de-loading | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230017 | Last priority | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230018 | Global auto start | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90230019 | Global auto stop | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90250000 | Stopping in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250001 | Starting in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250002 | Non-connected stop in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250003 | Already first priority | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250004 | Priority change not allowed | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250005 | GB open cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250006 | GB close cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250007 | Precautionary standby | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250008 | Connecting genset in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250009 | Genset starting - SG f [Hz] | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250010 | Genset synchronising - SG f [Hz] | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250011 | Any generator frequency missing | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250012 | Already last priority | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250013 | External start order | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250014 | Blackout due to CAN error | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250015 | Start engine and open MB | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90250016 | Open MB at ready engine | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90260000 | Generator L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90260001 | Busbar L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90260002 | Generator L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90260003 | Generator L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90260004 | Generator L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90260005 | Busbar L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90260006 | Busbar L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90260007 | Busbar L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90260008 | Mains breaker not closed | Texts related to controller operations / Alarm text (pop-ups and logs)
90260009 | Generator phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90260010 | Busbar phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90300000 | Base load | Texts related to controller operations / Parameter name
90300010 | Set point | Texts related to controller operations / Parameter name
90300020 | Minimum limit | Texts related to controller operations / Parameter name
90300030 | Maximum limit | Texts related to controller operations / Parameter name
90300040 | Enable SG blackout close | Texts related to controller operations / Parameter name
90300050 | SG-DG max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90300060 | SG-SG max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90300070 | Open point enabled | Texts related to controller operations / Parameter name
90300080 | Open when power below | Texts related to controller operations / Parameter name
90300090 | PTH connect load | Texts related to controller operations / Parameter name
90300100 | Enable | Texts related to controller operations / Miscellaneous text (various uses)
90300110 | Low frequency limit | Texts related to controller operations / Parameter name
90300120 | High frequency limit | Texts related to controller operations / Parameter name
90300130 | Low frequency limit | Texts related to controller operations / Parameter name
90300140 | High frequency limit | Texts related to controller operations / Parameter name
90300150 | Delay | Texts related to controller operations / Timer text
90300160 | Delay | Texts related to controller operations / Timer text
90300170 | SG-Hybrid max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90310000 | SGB close blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310010 | SGB close not blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310020 | PTH mode activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310030 | PTH mode deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310040 | Zero pitch activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310050 | Zero pitch deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310060 | SG fixed speed activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310070 | SG fixed speed deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310080 | SG genset start request (f [Hz]) | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90310090 | SG connect genset(s) request (f [Hz]) | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90320000 | SG-DG max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90320001 | SG-SG max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90320003 | SG fixed speed | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90330000 | SGB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90330001 | SGB open | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90330002 | Block SGB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90330003 | PTH mode | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90330004 | Zero pitch | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90330005 | SGB open without de-loading | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90340000 | SGB open not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90340001 | SGB close not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90340002 | SGB block not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90340003 | PTH mode not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90340004 | Zero pitch not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90340005 | SG fixed speed not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90340006 | SGB open without de-loading not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350000 | Load on SG too high (PTH) | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350001 | Pitch not zero | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350002 | PTH mode deactivates when breaker is opened | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350003 | PTH mode activates when breaker is opened | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350004 | SGB opening | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350005 | SG not ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350006 | SG ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350007 | SG running | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350008 | SG in operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350009 | SG in operation (base load) | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350010 | SG in PTH operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350011 | SGB closing | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350012 | SGB open cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350013 | SGB close cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350014 | SG-SG changeover aborted | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350015 | SG-SC changeover aborted | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350016 | SG ready for PTH operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350017 | SG genset start request | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350018 | SG connect genset(s) request | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350019 | Off | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350020 | Active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90350021 | Active with priority | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90400000 | SC-DG max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90400010 | SC-SG max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90400020 | SC-SC max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90400030 | Enable SC base load | Texts related to controller operations / Parameter name
90400040 | Set point | Texts related to controller operations / Parameter name
90400050 | Minimum limit | Texts related to controller operations / Parameter name
90400060 | Maximum limit | Texts related to controller operations / Parameter name
90400070 | Enable SC blackout close | Texts related to controller operations / Parameter name
90400080 | Minimum load on ship busbar | Texts related to controller operations / Parameter name
90400090 | Open point enabled | Texts related to controller operations / Parameter name
90400100 | Open when power below | Texts related to controller operations / Parameter name
90400110 | Ship-to-ship connect load | Texts related to controller operations / Parameter name
90400120 | Breaker action | Texts related to controller operations / Parameter name
90400130 | SC-Hybrid max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90410000 | SCB close blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90410010 | SCB close not blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90410020 | Ship-to-ship activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90410030 | Ship-to-ship deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90410040 | SCB action open | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90410050 | SCB action open without de-loading | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90420000 | SC-DG max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90420001 | SC-SG max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90420002 | SC-SC max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90420003 | SC-Hybrid max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90430000 | Ship-to-ship supply | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90430001 | SCB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90430002 | SCB open | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90430003 | Block SCB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90430004 | SCB open without de-loading | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90430005 | SCB action open | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90430006 | SCB action open without de-loading | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90440000 | SCB open not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90440001 | SCB close not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90440002 | SCB block not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90440003 | Ship-to-ship not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90440004 | SCB open without de-loading not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450000 | SCB opening | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450001 | Busbar V/Hz not OK | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450002 | Too little consumed power | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450003 | SCB closing | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450004 | SC not ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450005 | SC ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450006 | SC in operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450007 | SC in operation (base load) | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450008 | SC in ship-to-ship supply | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450009 | SCB open cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450010 | SCB close cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450011 | Shore connection V/Hz not OK | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450012 | Load on busbar too high | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450013 | SC-SC changeover aborted | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450014 | SC-SG changeover aborted | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450015 | SC ready for ship-to-ship supply | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450016 | Load on SC too high (ship-to-ship) | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450017 | Ship-to-ship deactivates when breaker is opened | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450018 | Ship-to-ship activates when breaker is opened | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450019 | SC base load disabled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450020 | SC overlap power too high | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90450021 | Any shore connection frequency missing | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90460000 | Busbar L1-L2-L3 wire break | Texts related to controller operations / Miscellaneous text (various uses)
90460001 | Shore connection L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90460002 | Busbar L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90460003 | Busbar L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90460004 | Busbar L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90460005 | Shore connection L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90460006 | Shore connection L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90460007 | Shore connection L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90460008 | Busbar phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90460009 | Shore phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90460010 | Select how to open the SC | Texts related to controller operations / Miscellaneous text (various uses)
90460011 | De-load: Open breaker with de-load | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90460012 | Open: Open without de-load | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90460015 | De-load | Texts related to controller operations / Miscellaneous text (various uses)
90460016 | Open | Texts related to controller operations / Real-time user interaction (mainly emulation)
90460018 | Cancel | Texts related to controller operations / Real-time user interaction (mainly emulation)
90460019 | Not enough available power to open without de-loading SCB | Texts related to controller operations / Miscellaneous text (various uses)
90500000 | Supply mode after connecting | Texts related to controller operations / Parameter name
90500010 | Enable BTB blackout close | Texts related to controller operations / Parameter name
90510000 | BTB close blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90510010 | BTB close not blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90510020 | DG supply activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90510030 | SG/SC supply activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90520000 | Closes a plant ring | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90520001 | Breaks a plant ring | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90530000 | BTB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90530001 | BTB open | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90530002 | Block BTB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90530003 | Stay on DG supply after BTB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90530004 | Stay on SG/SC supply after BTB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90530005 | BTB open without de-loading | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90540000 | BTB open not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90540001 | BTB close not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90540002 | BTB block not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90540003 | DG supply not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90540004 | SG/SC supply not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90540005 | BTB open without de-loading not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550000 | Sections cannot synchronise | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550001 | Not enough gensets for DG supply | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550002 | SG nominal power too low | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550003 | SC nominal power too low | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550004 | Ring connection not allowed | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550005 | Staying on DG supply | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550006 | Staying on SG/SC supply | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550007 | Not ready for operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550008 | Ready for operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550009 | BTB in operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550010 | BTB open cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550011 | BTB close cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550012 | Section cannot divide | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550013 | Stay on DG supply | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550014 | Stay on SG/SC supply | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550015 | Section A cannot become self-sustainable | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550016 | Section B cannot become self-sustainable | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550017 | SC-SC parallel not allowed | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550018 | De-load not possible | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550019 | Synchronisation not possible | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550020 | Blackout recovery not allowed | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550021 | Busbar A blocking | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550022 | Busbar B blocking | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550023 | Auto operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550024 | Ready auto operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550025 | Manual operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90550026 | Busbar blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90560000 | Busbar A L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90560001 | Busbar B L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90560002 | Busbar A L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90560003 | Busbar A L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90560004 | Busbar A L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90560005 | Busbar B L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90560006 | Busbar B L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90560007 | Busbar B L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90560008 | Busbar A phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90560009 | Busbar B phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90560010 | Reference A phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90560011 | Reference B phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90600000 | Blackout control | Texts related to controller operations / Parameter name
90600010 | Type | Texts related to controller operations / Parameter name
90600020 | Base load | Texts related to controller operations / Parameter name
90600030 | Mode | Texts related to controller operations / Parameter name
90600040 | Test time | Texts related to controller operations / Timer text
90600050 | Test sequence started | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90600060 | Test sequence ended | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90600070 | Test sequence interrupted due to blackout | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90600080 | EDG max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90600090 | EDG not ready for blackout | Texts related to controller operations / Alarm text (pop-ups and logs)
90600100 | Enable | Texts related to controller operations / Parameter name
90600110 | TB under-voltage timer | Texts related to controller operations / Timer text
90600120 | Enable | Texts related to controller operations / Parameter name
90610000 | Harbour operation activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90610010 | Harbour operation deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90610020 | TB close blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90610030 | TB close not blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90610040 | Harbour operation allowed | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90610050 | Harbour operation requested | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90620000 | EDG max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90620001 | Harbour operation active | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90620002 | EDG not ready for blackout | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630000 | Test genset | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630001 | TB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630002 | TB open | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630003 | Block TB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630004 | Harbour operation | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630005 | Main busbar is OK | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630006 | Allow harbour operation | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630007 | Reject harbour operation | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90630008 | Test sequence is active | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90640000 | Engine test not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90640001 | TB open not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90640002 | TB close not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90640003 | TB block not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90640004 | Harbour operation not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650000 | Blackout handling in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650001 | Busbar OK in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650002 | Open TB and start engine | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650003 | Start engine and open TB | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650004 | Not possible as non-sync EDG | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650005 | Engine test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650006 | Parallel test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650007 | Load take-over test | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650008 | Engine test - remaining | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650009 | Parallel test - remaining | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650010 | LTO test - remaining | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650011 | Test sequence cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650012 | TB open cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650013 | TB close cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650014 | Busbar OK input not active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650015 | Harbour operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650016 | Not possible as stand-alone EDG | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650017 | TB opened during de-load of GB | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650018 | Blackout detection in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650019 | Harbour operation requested | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650020 | Allow | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650021 | Reject | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650022 | Press Allow to allow harbour operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650023 | Press Reject to prevent harbour operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650024 | GB opened during de-load of MB | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650025 | MB opened during de-load of GB | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90650026 | In solo supply harbour operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90710000 | Breaker close activated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90710010 | Breaker close deactivated | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90760000 | In operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90760001 | Not ready for operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90760002 | Ready for operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90760003 | Trip breaker active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90760004 | Breaker close not possible | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90760005 | Sync check selected | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90760006 | Breaker not configured | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90800000 | Recovery selector time | Texts related to controller operations / Alarm text (pop-ups and logs)
90800010 | Recovery time fast | Texts related to controller operations / Timer text
90800020 | Recovery time slow | Texts related to controller operations / Timer text
90800030 | Voltage low | Texts related to controller operations / Parameter name
90800040 | Voltage high | Texts related to controller operations / Parameter name
90800050 | Frequency low | Texts related to controller operations / Parameter name
90800060 | Frequency high | Texts related to controller operations / Parameter name
90800070 | Enable supervision | Texts related to controller operations / Parameter name
90800080 | Mains supervision alarm | Texts related to controller operations / Alarm text (pop-ups and logs)
90800090 | MB breaker type | Texts related to controller operations / Parameter name
90800100 | ID to run configuration failure | Texts related to controller operations / Alarm text (pop-ups and logs)
90800110 | Measurement configuration | Texts related to controller operations / Parameter name
90810000 | MB close blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90810010 | MB close not blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90810020 | Mains OK input high | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90810030 | Mains OK input low | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90810040 | Mains automatic transfer switch active | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90820000 | Genset in parallel | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90820001 | Mains error | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90820002 | Mains recovery fast | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90820003 | Mains recovery slow | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90830000 | MB open | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90830001 | MB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90830002 | Block MB close | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90830003 | Open MB without de-loading | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90830004 | Open TB without de-loading | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90850000 | MB close cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90850001 | MB open cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90850002 | Mains not ready for operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90850003 | Mains ready for operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90850004 | Mains in operation | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90850005 | Mains failure | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90850006 | Mains voltage OK in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90850007 | Mains frequency OK in | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90860001 | Mains L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90860002 | Mains L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90860003 | Mains L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90860004 | Mains L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90860005 | Mains V/Hz not OK | Texts related to controller operations / Alarm text (pop-ups and logs)
90860006 | Mains phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
90860007 | Mains synchronisation OK in | Texts related to controller operations / Alarm text (pop-ups and logs)
90860008 | Mains synchronisation inhibit | Texts related to controller operations / Alarm text (pop-ups and logs)
90860009 | Phase sequence error mains | Texts related to controller operations / Alarm text (pop-ups and logs)
90860010 | Phase sequence error busbar/mains | Texts related to controller operations / Alarm text (pop-ups and logs)
90900020 | Hybrid-SG max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90900030 | Hybrid-SC max. parallel time | Texts related to controller operations / Alarm text (pop-ups and logs)
90900100 | Standby request failure | Texts related to controller operations / Miscellaneous text (various uses)
90900110 | Standby acknowledge timeout | Texts related to controller operations / Miscellaneous text (various uses)
90900120 | Acknowledge pulse length | Texts related to controller operations / Miscellaneous text (various uses)
90900130 | PTI request failure | Texts related to controller operations / Miscellaneous text (various uses)
90900140 | PTI acknowledge timeout | Texts related to controller operations / Miscellaneous text (various uses)
90900150 | Acknowledge pulse length | Texts related to controller operations / Miscellaneous text (various uses)
90900160 | PTO request failure | Texts related to controller operations / Miscellaneous text (various uses)
90900170 | PTO acknowledge timeout | Texts related to controller operations / Miscellaneous text (various uses)
90900180 | Acknowledge pulse length | Texts related to controller operations / Miscellaneous text (various uses)
90900190 | Nominal load | Texts related to controller operations / Miscellaneous text (various uses)
90910000 | Standby running | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910010 | Standby requested | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910020 | PTI running | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910030 | PTI requested | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910040 | PTO running | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910050 | PTO requested | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910060 | Breaker close blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910070 | Breaker close not blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910080 | Breaker open blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90910090 | Breaker open not blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90920000 | Hybrid-SG max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920001 | Hybrid-SC max. parallel time | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920100 | Power direction state | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920150 | Standby request (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920151 | Standby ready (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920152 | Standby running (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920153 | Standby acknowledge (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920154 | Standby state (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920155 | Standby requested (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920156 | Standby acknowledged (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920157 | Standby request failure (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920158 | Standby acknowledge timeout (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920159 | Standby active (Hybrid) | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920200 | PTI request | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920201 | PTI ready | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920202 | PTI running | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920203 | PTI acknowledge | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920204 | PTI state | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920205 | PTI requested | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920206 | PTI acknowledged | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920207 | PTI request failure | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920208 | PTI acknowledge timeout | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920209 | PTI active | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920250 | PTO request | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920251 | PTO ready | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920252 | PTO running | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920253 | PTO acknowledge | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920254 | PTO state | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920255 | PTO requested | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920256 | PTO acknowledged | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920257 | PTO request failure | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920258 | PTO acknowledge timeout | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90920259 | PTO active | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90930000 | Block breaker open | Texts related to controller operations / Assignable function (input/output config menus, Modbus)
90940000 | Inverter start not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90940001 | Inverter stop not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90940003 | Breaker open not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90940004 | Breaker close not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90940005 | Connect (start/close) not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90940006 | Disconnect (open/stop) not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90940010 | Breaker open without de-loading not possible in SWBD | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950000 | Load too high | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950005 | Breaker open cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950006 | Breaker close cancelled | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950010 | Standby blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950011 | Standby ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950012 | Standby running | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950020 | PTO blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950021 | PTO ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950022 | PTO running | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950030 | PTI blocked | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950031 | PTI ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950032 | PTI running | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950033 | Standby not ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950034 | PTO not ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950035 | PTI not ready | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950036 | Alarm blocking standby request | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950037 | Alarm blocking PTO request | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950038 | Alarm blocking PTI request | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950039 | Standby requested | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950040 | PTO requested | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950041 | PTI requested | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950042 | Standby transitioning to PTI | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950043 | Standby transitioning to PTO | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950044 | PTI transitioning to standby | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950045 | PTI transitioning to PTO | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950046 | PTO transitioning to standby | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90950047 | PTO transitioning to PTI | Texts related to controller operations / Event text (pop-ups, logs and status texts)
90960000 | Start inverter | Texts related to controller operations / Alarm text (pop-ups and logs)
90960001 | Stop inverter | Texts related to controller operations / Alarm text (pop-ups and logs)
90960002 | Connect (inverter/breaker) | Texts related to controller operations / Alarm text (pop-ups and logs)
90960003 | Disconnect (inverter/breaker) | Texts related to controller operations / Alarm text (pop-ups and logs)
90960004 | Block inverter start | Texts related to controller operations / Alarm text (pop-ups and logs)
90960005 | Reset block inverter start | Texts related to controller operations / Alarm text (pop-ups and logs)
90960006 | Inverter L1-L2-L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90960007 | Inverter L1 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90960008 | Inverter L2 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90960009 | Inverter L3 wire break | Texts related to controller operations / Alarm text (pop-ups and logs)
90960010 | Inverter phase sequence error | Texts related to controller operations / Alarm text (pop-ups and logs)
100001100 | Emergency stop | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100001101 | Emergency stop | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100010000 | Emergency stop | Texts related to system operational status / Alarm text (pop-ups and logs)
100020000 | PCM clock battery failure | Texts related to system operational status / Alarm text (pop-ups and logs)
100021000 | PCM clock battery failure | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100030000 | Controller temperature too high | Texts related to system operational status / Alarm text (pop-ups and logs)
100031000 | Controller temperature too high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100040000 | PSM3.1 1 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100040010 | PSM3.1 1 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100040020 | Diode offset | Texts related to system operational status / Parameter name
100041000 | PSM3.1 1 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100041001 | PSM3.1 1 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100041002 | PSM3.1 1 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100042000 | PSM3.2 1 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100042010 | PSM3.2 1 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100042020 | Diode offset | Texts related to system operational status / Parameter name
100043000 | PSM3.2 1 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100043001 | PSM3.2 1 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100043002 | PSM3.2 1 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100044000 | PSM3.2 2 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100044010 | PSM3.2 2 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100044020 | Diode offset | Texts related to system operational status / Parameter name
100045000 | PSM3.2 2 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100045001 | PSM3.2 2 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100045002 | PSM3.2 2 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100046000 | PSM3.2 3 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100046010 | PSM3.2 3 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100046020 | Diode offset | Texts related to system operational status / Parameter name
100047000 | PSM3.2 3 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100047001 | PSM3.2 3 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100047002 | PSM3.2 3 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100048000 | EIM3.1 1 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100048010 | EIM3.1 1 supply voltage low or missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100048020 | Diode offset | Texts related to system operational status / Parameter name
100049000 | EIM3.1 1 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100049001 | EIM3.1 1 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100049002 | EIM3.1 1 supply voltage low or missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100050000 | EIM3.1 2 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100050010 | EIM3.1 2 supply voltage low or missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100050020 | Diode offset | Texts related to system operational status / Parameter name
100051000 | EIM3.1 2 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100051001 | EIM3.1 2 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100051002 | EIM3.1 2 supply voltage low or missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100052000 | EIM3.1 3 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100052010 | EIM3.1 3 supply voltage low or missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100052020 | Diode offset | Texts related to system operational status / Parameter name
100053000 | EIM3.1 3 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100053001 | EIM3.1 3 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100053002 | EIM3.1 3 supply voltage low or missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100054000 | EIM3.1 4 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100054010 | EIM3.1 4 supply voltage low or missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100054020 | Diode offset | Texts related to system operational status / Parameter name
100056000 | EIM3.1 4 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100056001 | EIM3.1 4 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100056002 | EIM3.1 4 supply voltage low or missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100057000 | EIM3.1 5 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100057010 | EIM3.1 5 supply voltage low or missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100057020 | Diode offset | Texts related to system operational status / Parameter name
100058000 | EIM3.1 5 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100058001 | EIM3.1 5 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100058002 | EIM3.1 5 supply voltage low or missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100059000 | EIM3.1 1 relay 4 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100060000 | EIM3.1 1 relay 4 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100060001 | EIM3.1 1 relay 4 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100061000 | EIM3.1 2 relay 4 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100062000 | EIM3.1 2 relay 4 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100062001 | EIM3.1 2 relay 4 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100063000 | EIM3.1 3 relay 4 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100064000 | EIM3.1 3 relay 4 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100064001 | EIM3.1 3 relay 4 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100065000 | EIM3.1 4 relay 4 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100066000 | EIM3.1 4 relay 4 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100066001 | EIM3.1 4 relay 4 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100067000 | EIM3.1 5 relay 4 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100068000 | EIM3.1 5 relay 4 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100068001 | EIM3.1 5 relay 4 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100070000 | AC protections not running | Texts related to system operational status / Alarm text (pop-ups and logs)
100070010 | AC data is missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100071001 | AC protections not running | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071002 | AC data is missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071100 | AC protections not running | Texts related to system operational status / Alarm text (pop-ups and logs)
100071110 | AC data is missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100071201 | AC protections not running | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071202 | AC data is missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071300 | AC protections not running | Texts related to system operational status / Alarm text (pop-ups and logs)
100071310 | AC data is missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100071401 | AC protections not running | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071402 | AC data is missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071500 | AC protections not running | Texts related to system operational status / Alarm text (pop-ups and logs)
100071510 | AC data is missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100071601 | AC protections not running | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071602 | AC data is missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071700 | AC protections not running | Texts related to system operational status / Alarm text (pop-ups and logs)
100071710 | AC data is missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100071801 | AC protections not running | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100071802 | AC data is missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100073000 | AC protections not running (differential current) | Texts related to system operational status / Alarm text (pop-ups and logs)
100073010 | AC data is missing (differential current) | Texts related to system operational status / Alarm text (pop-ups and logs)
100073101 | AC protections not running (differential current) | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100073102 | AC data is missing (differential current) | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100078000 | GAM3.2 1 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100078010 | GAM3.2 1 supply voltage low or missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100078020 | Diode offset | Texts related to system operational status / Parameter name
100079000 | GAM3.2 1 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100079001 | GAM3.2 1 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100079002 | GAM3.2 1 supply voltage low or missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100080000 | GAM3.2 2 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100080010 | GAM3.2 2 supply voltage low or missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100080020 | Diode offset | Texts related to system operational status / Parameter name
100081000 | GAM3.2 2 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100081001 | GAM3.2 2 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100081002 | GAM3.2 2 supply voltage low or missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100082000 | GAM3.2 3 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100082010 | GAM3.2 3 supply voltage low or missing | Texts related to system operational status / Alarm text (pop-ups and logs)
100082020 | Diode offset | Texts related to system operational status / Parameter name
100083000 | GAM3.2 3 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100083001 | GAM3.2 3 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100083002 | GAM3.2 3 supply voltage low or missing | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100084000 | PSM3.2 4 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100084010 | PSM3.2 4 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100084020 | Diode offset | Texts related to system operational status / Parameter name
100085000 | PSM3.2 4 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100085001 | PSM3.2 4 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100085002 | PSM3.2 4 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100086000 | PSM3.2 5 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100086010 | PSM3.2 5 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100086020 | Diode offset | Texts related to system operational status / Parameter name
100087000 | PSM3.2 5 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100087001 | PSM3.2 5 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100087002 | PSM3.2 5 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100088000 | PSM3.2 6 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100088010 | PSM3.2 6 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100088020 | Diode offset | Texts related to system operational status / Parameter name
100089000 | PSM3.2 6 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100089001 | PSM3.2 6 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100089002 | PSM3.2 6 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100090000 | PSM3.2 7 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100090010 | PSM3.2 7 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100090020 | Diode offset | Texts related to system operational status / Parameter name
100091000 | PSM3.2 7 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100091001 | PSM3.2 7 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100091002 | PSM3.2 7 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100092000 | PSM3.2 8 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100092010 | PSM3.2 8 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100092020 | Diode offset | Texts related to system operational status / Parameter name
100093000 | PSM3.2 8 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100093001 | PSM3.2 8 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100093002 | PSM3.2 8 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100094000 | PSM3.2 9 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100094010 | PSM3.2 9 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100094020 | Diode offset | Texts related to system operational status / Parameter name
100095000 | PSM3.2 9 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100095001 | PSM3.2 9 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100095002 | PSM3.2 9 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100096000 | PCM2.1 supply voltage high | Texts related to system operational status / Alarm text (pop-ups and logs)
100096010 | PCM2.1 supply voltage low | Texts related to system operational status / Alarm text (pop-ups and logs)
100096020 | Diode offset | Texts related to system operational status / Parameter name
100097000 | PCM2.1 supply voltage | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100097001 | PCM2.1 supply voltage high | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100097002 | PCM2.1 supply voltage low | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100100000 | MIO2.1 relay 9 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100100100 | MIO2.1 relay 10 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100100200 | MIO2.1 relay 11 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100100300 | MIO2.1 relay 12 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100100400 | MIO2.1 relay 13 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100100500 | MIO2.1 relay 14 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100100600 | MIO2.1 relay 15 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100100700 | MIO2.1 relay 16 wire break | Texts related to system operational status / Alarm text (pop-ups and logs)
100101000 | MIO2.1 relay 9 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101001 | MIO2.1 relay 9 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101010 | MIO2.1 relay 10 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101011 | MIO2.1 relay 10 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101020 | MIO2.1 relay 11 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101021 | MIO2.1 relay 11 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101030 | MIO2.1 relay 12 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101031 | MIO2.1 relay 12 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101040 | MIO2.1 relay 13 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101041 | MIO2.1 relay 13 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101050 | MIO2.1 relay 14 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101051 | MIO2.1 relay 14 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101060 | MIO2.1 relay 15 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101061 | MIO2.1 relay 15 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101070 | MIO2.1 relay 16 wire break detection | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
100101071 | MIO2.1 relay 16 wire break | Texts related to system operational status / Assignable function (input/output config menus, Modbus)
101000000 | Controller joined plant successfully | Texts related to feature: / Status text (info lines)
101000010 | Controller left plant successfully | Texts related to feature: / Status text (info lines)
101000020 | Plant reset successfully | Texts related to feature: / Status text (info lines)
101001000 | Join | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001001 | Leave | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001002 | Reset | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001003 | Ready to join | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001004 | Ready to leave | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001005 | Ready to reset | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001006 | Number of controllers in network | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001007 | Number of controllers in plant | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001008 | Number of groups in network | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001009 | Number of groups in plant | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001010 | Part of quick-connect plant | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101001011 | Not part of quick-connect plant | Texts related to feature: / Assignable function (input/output config menus, Modbus)
101002000 | Join | Texts related to feature: / Status text (info lines)
101002001 | Do you want to join the single-line diagram? | Texts related to feature: / Status text (info lines)
101002002 | Leave | Texts related to feature: / Status text (info lines)
101002003 | Do you want to leave the current single-line diagram? | Texts related to feature: / Status text (info lines)
101002004 | Leave not possible | Texts related to feature: / Status text (info lines)
101002005 | Not part of quick-connect plant | Texts related to feature: / Status text (info lines)
101002006 | Not part of plant | Texts related to feature: / Status text (info lines)
101002007 | Join not possible | Texts related to feature: / Status text (info lines)
101002008 | Already part of quick-connect plant | Texts related to feature: / Status text (info lines)
101002009 | Not possible | Texts related to feature: / Status text (info lines)
101002010 | Quick-connect not possible (no quick-connect points in single-line diagram) | Texts related to feature: / Status text (info lines)
101002011 | Group structure is not the same as rest of the plant | Texts related to feature: / Status text (info lines)
101002012 | Reconfigure not possible | Texts related to feature: / Status text (info lines)
101002013 | Group ID already in quick-connect plant | Texts related to feature: / Status text (info lines)
101002014 | Feeder is connected while changing plant | Texts related to feature: / Status text (info lines)
101002015 | Feeder is synchronising while changing plant | Texts related to feature: / Status text (info lines)
101002016 | Feeder is de-loading while changing plant | Texts related to feature: / Status text (info lines)
110000000 | Any bus tie breaker position failure | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000010 | Duplicate controller ID | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000020 | Missing all controllers | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000030 | Missing any controller | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000040 | Any tie breaker position failure | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000050 | PMS disabled due to an error | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000060 | Controller ID not configured | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000070 | Mode | Texts related to PMS operational behaviour / Parameter name
110000080 | Mode | Texts related to PMS operational behaviour / Parameter name
110000090 | Missing controllers | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000100 | Any mains breaker position failure | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000110 | Data loss from a controller | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000120 | Data loss on DEIF network | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000130 | High traffic to DEIF network | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000140 | Range | Texts related to PMS operational behaviour / Parameter name
110000150 | Missing any genset controller | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000160 | Missing any mains controller | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000170 | Missing any bus tie controller | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000180 | Can ID not available | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000190 | Duplicated CAN IDs | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000200 | CAN transmission fail PMS line 1 | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000210 | CAN transmission fail PMS line 2 | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110000220 | Internal CAN protocol | Texts related to PMS operational behaviour / Parameter name
110000230 | Busbar blocked due to position failure | Texts related to PMS operational behaviour / Parameter name
110000240 | Busbar A blocked due to position failure | Texts related to PMS operational behaviour / Parameter name
110000250 | Busbar B blocked due to position failure | Texts related to PMS operational behaviour / Parameter name
110000270 | Start generator | Texts related to PMS operational behaviour / Parameter name
110000280 | Minimum load | Texts related to PMS operational behaviour / Parameter name
110000290 | Stop generator | Texts related to PMS operational behaviour / Parameter name
110000300 | Selection | Texts related to PMS operational behaviour / Parameter name
110000310 | Controller settings cos phi | Texts related to PMS operational behaviour / Parameter name
110000320 | Controller settings cos phi | Texts related to PMS operational behaviour / Parameter name
110000330 | Controller settings cos phi | Texts related to PMS operational behaviour / Parameter name
110000340 | Controller settings Q | Texts related to PMS operational behaviour / Parameter name
110000350 | Controller settings cos phi or Q | Texts related to PMS operational behaviour / Parameter name
110000360 | Minimum load | Texts related to PMS operational behaviour / Parameter name
110000370 | Start/stop | Texts related to PMS operational behaviour / Parameter name
110000410 | Load-dependent start internal | Texts related to PMS operational behaviour / Parameter name
110000430 | BTB 33 position failure | Texts related to PMS operational behaviour / Miscellaneous text (various uses)
110000440 | BTB 34 position failure | Texts related to PMS operational behaviour / Miscellaneous text (various uses)
110000450 | BTB 35 position failure | Texts related to PMS operational behaviour / Miscellaneous text (various uses)
110000460 | BTB 36 position failure | Texts related to PMS operational behaviour / Miscellaneous text (various uses)
110000470 | BTB 37 position failure | Texts related to PMS operational behaviour / Miscellaneous text (various uses)
110000480 | BTB 38 position failure | Texts related to PMS operational behaviour / Miscellaneous text (various uses)
110000490 | BTB 39 position failure | Texts related to PMS operational behaviour / Miscellaneous text (various uses)
110000500 | BTB 40 position failure | Texts related to PMS operational behaviour / Miscellaneous text (various uses)
110000510 | Offset 1 | Texts related to PMS operational behaviour / Parameter name
110000520 | Offset 2 | Texts related to PMS operational behaviour / Parameter name
110000530 | Offset 3 | Texts related to PMS operational behaviour / Parameter name
110000540 | Offset 1 | Texts related to PMS operational behaviour / Parameter name
110000550 | Offset 1 | Texts related to PMS operational behaviour / Parameter name
110000560 | Offset 2 | Texts related to PMS operational behaviour / Parameter name
110000570 | Offset 2 | Texts related to PMS operational behaviour / Parameter name
110000580 | Offset 3 | Texts related to PMS operational behaviour / Parameter name
110000590 | Offset 3 | Texts related to PMS operational behaviour / Parameter name
110000600 | Mains power | Texts related to PMS operational behaviour / Parameter name
110000610 | Mains power | Texts related to PMS operational behaviour / Parameter name
110000620 | Mains power | Texts related to PMS operational behaviour / Parameter name
110002000 | DEIF network redundancy broken | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002010 | Blackout detection mismatch | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002020 | Network protocol incompatible | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002030 | System power management network error | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002040 | Ring close allowed | Texts related to PMS operational behaviour / Parameter name
110002050 | DEIF network top ring redundancy broken | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002060 | Group alarm | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002070 | NTP server 1 could not connect | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002080 | NTP server 1 is not responding | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002090 | NTP server 2 could not connect | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002100 | NTP server 2 is not responding | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002110 | No NTP server time synchronisation | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002120 | No NTP server(s) connected | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002130 | CAN-A bus off | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002140 | CAN-B bus off | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002160 | Genset mode | Texts related to PMS operational behaviour / Parameter name
110002170 | Plant mode | Texts related to PMS operational behaviour / Parameter name
110002190 | Store common settings | Texts related to PMS operational behaviour / Parameter name
110002210 | Back synchronising | Texts related to PMS operational behaviour / Parameter name
110002220 | Synchronisation to mains | Texts related to PMS operational behaviour / Parameter name
110002230 | Parallel | Texts related to PMS operational behaviour / Parameter name
110002240 | No break transfer | Texts related to PMS operational behaviour / Parameter name
110002250 | Auto switch | Texts related to PMS operational behaviour / Parameter name
110002260 | Run type | Texts related to PMS operational behaviour / Parameter name
110002270 | ID to run | Texts related to PMS operational behaviour / Parameter name
110002280 | MB failure start | Texts related to PMS operational behaviour / Parameter name
110002290 | TB open point | Texts related to PMS operational behaviour / Parameter name
110002300 | Power capacity | Texts related to PMS operational behaviour / Parameter name
110002310 | Power capacity overrule | Texts related to PMS operational behaviour / Parameter name
110002320 | Power capacity overrule | Texts related to PMS operational behaviour / Parameter name
110002330 | Exclude run all | Texts related to PMS operational behaviour / Parameter name
110002340 | DEIF network fork detected | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002350 | DEIF network top ring fork detected | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002360 | DEIF network has only one connection | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110002370 | DEIF network top ring has only one connection | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110100000 | Blackout detection mismatch | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100001 | DEIF network redundancy broken | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100002 | Network protocol incompatible | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100003 | Any bus tie breaker position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100004 | Duplicate controller ID | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100005 | Missing all controllers | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100006 | Missing any controller | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100007 | Any tie breaker position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100008 | PMS disabled due to an error | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100009 | Controller ID not configured | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100010 | Maximum allowed controllers to missing | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100011 | DEIF network top ring redundancy broken | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100012 | Group alarm | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100013 | Group alarm | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100014 | NTP server 1 could not connect | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100015 | NTP server 1 is not responding | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100016 | Load-dependent stop blocked | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100017 | Global auto start active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100018 | NTP server 2 could not connect | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100019 | NTP server 2 is not responding | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100020 | No NTP server(s) connected | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100021 | No NTP server time synchronisation | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100022 | CAN-A bus off | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100023 | CAN-B bus off | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100024 | Active offset 1 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100025 | Active offset 2 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100026 | Active offset 3 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100027 | Active offset 1 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100028 | Active offset 2 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100029 | Active offset 3 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100030 | Activate external power set point | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100031 | Deactivate external power set point | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100032 | External power set point is selected | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100033 | Activate external power set point | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100034 | Deactivate external power set point | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100035 | DEIF network fork detected | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110100036 | DEIF network top ring fork detected | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110100037 | DEIF network has only one connection | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110100038 | DEIF network top ring has only one connection | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110100100 | Section ¦ PMS P avail. | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100101 | Section ¦ PMS P used | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100102 | Section ¦ PMS P nom. | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100103 | Section ¦ PMS P avail. | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100104 | Controller ID | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100105 | Section ¦ PMS P used | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100106 | Section ¦ Conn. P avail. | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100107 | Section ¦ Conn. P used | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100108 | Section ¦ Conn. P nom. | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100109 | Section ¦ Conn. P avail. | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100110 | Section ¦ Conn. P used | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100111 | Secured mode active in section | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100112 | Precautionary genset start in section | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100113 | Dynamic section ID | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100114 | Number of feeders connected in PMS | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100115 | Load-dependent start timer running | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100116 | Load-dependent stop timer running | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100117 | Busbar blocked due to position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100118 | Busbar A blocked due to position failure output | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100119 | Busbar B blocked due to position failure output | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100200 | Section ¦ P produced | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100201 | Section ¦ Q produced | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100202 | Section ¦ S produced | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100203 | Section ¦ Power factor | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100204 | Section ¦ P used | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100205 | Section ¦ Q used | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100206 | Section ¦ S used | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100210 | Plant ¦ P produced | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100211 | Plant ¦ Q produced | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100212 | Plant ¦ S produced | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100213 | Plant ¦ Power factor | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100300 | Section ¦ P nominal | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100301 | Section ¦ Q nominal | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100302 | Section ¦ S nominal | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100400 | Section ¦ P available | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100401 | Section ¦ Q available | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100402 | Section ¦ S available | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100410 | Section ¦ P available | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100411 | Section ¦ Q available | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100412 | Section ¦ S available | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100413 | BTB 33 position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100414 | BTB 34 position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100415 | BTB 35 position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100416 | BTB 36 position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100417 | BTB 37 position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100418 | BTB 38 position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100419 | BTB 39 position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110100420 | BTB 40 position failure | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110200000 | Press again for blackout | Texts related to PMS operational behaviour / Parameter name
110200001 | Section | Texts related to PMS operational behaviour / Parameter name
110200002 | Plant | Texts related to PMS operational behaviour / Parameter name
110200003 | Missing controller(s) in group | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110200004 | Missing controller | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110200005 | Missing controller ID %s | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110200006 | Off | Texts related to PMS operational behaviour / Parameter name
110200007 | On | Texts related to PMS operational behaviour / Parameter name
110200008 | Superior | Texts related to PMS operational behaviour / Parameter name
110200009 | Fixed Q | Texts related to PMS operational behaviour / Parameter name
110200010 | Fixed for DG(s) | Texts related to PMS operational behaviour / Parameter name
110200011 | Fixed for import/export | Texts related to PMS operational behaviour / Parameter name
110200012 | Local update | Texts related to PMS operational behaviour / Parameter name
110200013 | Update all | Texts related to PMS operational behaviour / Parameter name
110200014 | Fixed cos phi | Texts related to PMS operational behaviour / Parameter name
110200019 | Primary CAN missing ID %s | Texts related to PMS operational behaviour / Parameter name
110200020 | Secondary CAN missing ID %s | Texts related to PMS operational behaviour / Parameter name
110300000 | AMF - NO REG | Texts related to PMS operational behaviour / Status text (info lines)
110300001 | AMF - MANUAL | Texts related to PMS operational behaviour / Status text (info lines)
110300002 | AMF - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300003 | Ready for AMF - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300004 | AMF is active - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300010 | Island - NO REG | Texts related to PMS operational behaviour / Status text (info lines)
110300011 | Island - MANUAL | Texts related to PMS operational behaviour / Status text (info lines)
110300012 | Island - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300013 | Ready for Island - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300014 | Island is active - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300020 | Peak shaving - NO REG | Texts related to PMS operational behaviour / Status text (info lines)
110300021 | Peak shaving - MANUAL | Texts related to PMS operational behaviour / Status text (info lines)
110300022 | Peak shaving - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300023 | Ready for Peak shaving - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300024 | Peak shaving is active - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300030 | Fixed power - NO REG | Texts related to PMS operational behaviour / Status text (info lines)
110300031 | Fixed power - MANUAL | Texts related to PMS operational behaviour / Status text (info lines)
110300032 | Fixed power - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300033 | Ready for Fixed power - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300034 | Fixed power is active - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300040 | Mains power export - NO REG | Texts related to PMS operational behaviour / Status text (info lines)
110300041 | Mains power export - MANUAL | Texts related to PMS operational behaviour / Status text (info lines)
110300042 | Mains power export - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300043 | Ready for Mains power export - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300044 | Mains power export is active - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300050 | Load take over - NO REG | Texts related to PMS operational behaviour / Status text (info lines)
110300051 | Load take over - MANUAL | Texts related to PMS operational behaviour / Status text (info lines)
110300052 | Load take over - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300053 | Ready for Load take over - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110300054 | Load take over is active - AUTO | Texts related to PMS operational behaviour / Status text (info lines)
110301000 | Simple test | Texts related to PMS operational behaviour / Status text (info lines)
110301001 | Load test | Texts related to PMS operational behaviour / Status text (info lines)
110301002 | Full test | Texts related to PMS operational behaviour / Status text (info lines)
110500000 | Power management rules to activate | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500010 | Power management rules activated | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500020 | Different power management rules activated | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110500030 | Power management rule changed | Texts related to PMS operational behaviour / Event text (pop-ups, logs and status texts)
110500100 | Deactivate selected power management rule | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500110 | Activate power management rule 1 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500120 | Activate power management rule 2 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500130 | Activate power management rule 3 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500140 | Activate power management rule 4 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500150 | Activate power management rule 5 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500160 | Activate power management rule 6 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500170 | Activate power management rule 7 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500180 | Activate power management rule 8 | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500210 | Power management rule 1 active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500220 | Power management rule 2 active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500230 | Power management rule 3 active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500240 | Power management rule 4 active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500250 | Power management rule 5 active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500260 | Power management rule 6 active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500270 | Power management rule 7 active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110500280 | Power management rule 8 active | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110600000 | Priority error | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110600010 | Method | Texts related to PMS operational behaviour / Parameter name
110600020 | Activate priority update | Texts related to PMS operational behaviour / Parameter name
110600030 | Method | Texts related to PMS operational behaviour / Parameter name
110600040 | Swap timer | Texts related to PMS operational behaviour / Parameter name
110600050 | Fixed time enable | Texts related to PMS operational behaviour / Parameter name
110600060 | Fixed start hour | Texts related to PMS operational behaviour / Parameter name
110600070 | Fixed times/day | Texts related to PMS operational behaviour / Parameter name
110600080 | Floating time enable | Texts related to PMS operational behaviour / Parameter name
110600090 | Floating max. hours between running hours | Texts related to PMS operational behaviour / Parameter name
110600100 | Automatic priority swap hours | Texts related to PMS operational behaviour / An assignable function (CustomLogic)
110600110 | Transmit | Texts related to PMS operational behaviour / Parameter name
110650000 | Priority in section | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110650001 | Manual priority | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110650003 | Activate priority update | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110650004 | Fixed timer trigger | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110650005 | Floating timer trigger | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110650006 | Priority has changed | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110670000 | Manual | Texts related to PMS operational behaviour / Parameter name
110670001 | Delayed priority shift | Texts related to PMS operational behaviour / Parameter name
110670002 | Dynamic | Texts related to PMS operational behaviour / Parameter name
110670003 | Running hours | Texts related to PMS operational behaviour / Parameter name
110670004 | Total counter | Texts related to PMS operational behaviour / Parameter name
110670015 | Trip counter | Texts related to PMS operational behaviour / Parameter name
110670016 | Trip counter %s | Texts related to PMS operational behaviour / Parameter name
110670019 | Manual absolute | Texts related to PMS operational behaviour / Parameter name
110670020 | Fuel optimisation | Texts related to PMS operational behaviour / Parameter name
110670021 | Manual relative | Texts related to PMS operational behaviour / Parameter name
110670022 | Fuel optimisation + running hours | Texts related to PMS operational behaviour / Parameter name
110670025 | Priority %s | Texts related to PMS operational behaviour / Parameter name
110695000 | %s position failure | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110695001 | %s opened | Texts related to PMS operational behaviour / Event text (pop-ups, logs and status texts)
110695002 | %s closed | Texts related to PMS operational behaviour / Event text (pop-ups, logs and status texts)
110695003 | %s operations | Texts related to PMS operational behaviour / An assignable function (CustomLogic)
110695004 | %s feedback mismatch | Texts related to PMS operational behaviour / Alarm text (pop-ups and logs)
110695005 | %s open | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110695006 | %s closed | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110695007 | %s is open | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110695008 | %s is closed | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110695009 | %s state | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110695011 | %s busbar A state | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110695012 | %s busbar B state | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110800000 | ICC input %s | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
110900000 | ICC output %s | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
111000000 | ICC input %s | Texts related to PMS operational behaviour / Assignable function (input/output config menus, Modbus)
124000000 | Pulse | Texts related to feature: / Parameter configuration (selected from a list)
124000001 | Continuous | Texts related to feature: / Parameter configuration (selected from a list)
124000010 | %s reservation not possible | Texts related to feature: / Alarm text (pop-ups and logs)
124000011 | %s feedback timeout | Texts related to feature: / Alarm text (pop-ups and logs)
124000012 | Initial load | Texts related to feature: / Parameter name
124000013 | Nominal load | Texts related to feature: / Parameter name
124000014 | Power factor | Texts related to feature: / Parameter name
124000015 | Pulse width | Texts related to feature: / Parameter name
124000016 | Type | Texts related to feature: / Parameter name
124000017 | Delay | Texts related to feature: / Timer text
124000020 | Request | Texts related to feature: / Parameter configuration (selected from a list)
124000021 | Acknowledge | Texts related to feature: / Parameter configuration (selected from a list)
124000022 | Feedback | Texts related to feature: / Parameter configuration (selected from a list)
124000023 | Feedback | Texts related to feature: / Parameter configuration (selected from a list)
124000024 | Load | Texts related to feature: / Parameter configuration (selected from a list)
124000025 | Load | Texts related to feature: / Parameter configuration (selected from a list)
124000026 | State | Texts related to feature: / Parameter configuration (selected from a list)
124000027 | Reservation not possible | Texts related to feature: / Parameter configuration (selected from a list)
124000028 | Feedback timeout | Texts related to feature: / Parameter configuration (selected from a list)
125000000 | NEL 1 over-current | Texts related to feature: / Alarm text (pop-ups and logs)
125000010 | NEL 1 under-frequency | Texts related to feature: / Alarm text (pop-ups and logs)
125000020 | NEL 1 overload 1 | Texts related to feature: / Alarm text (pop-ups and logs)
125000030 | NEL 1 overload 2 | Texts related to feature: / Alarm text (pop-ups and logs)
125000040 | NEL 1 reactive overload | Texts related to feature: / Alarm text (pop-ups and logs)
125000050 | Trip when breaker trips | Texts related to feature: / Parameter name
125017000 | NEL 1 trip changed | Texts related to feature: / Event text (pop-ups, logs and status texts)
125019000 | Non-essential load trip 1 | Texts related to feature: / Assignable function (input/output config menus, Modbus)
125020000 | NEL 2 over-current | Texts related to feature: / Alarm text (pop-ups and logs)
125020010 | NEL 2 under-frequency | Texts related to feature: / Alarm text (pop-ups and logs)
125020020 | NEL 2 overload 1 | Texts related to feature: / Alarm text (pop-ups and logs)
125020030 | NEL 2 overload 2 | Texts related to feature: / Alarm text (pop-ups and logs)
125020040 | NEL 2 reactive overload | Texts related to feature: / Alarm text (pop-ups and logs)
125020050 | Trip when breaker trips | Texts related to feature: / Parameter name
125027000 | NEL 2 trip changed | Texts related to feature: / Event text (pop-ups, logs and status texts)
125029000 | Non-essential load trip 2 | Texts related to feature: / Assignable function (input/output config menus, Modbus)
125030000 | NEL 3 over-current | Texts related to feature: / Alarm text (pop-ups and logs)
125030010 | NEL 3 under-frequency | Texts related to feature: / Alarm text (pop-ups and logs)
125030020 | NEL 3 overload 1 | Texts related to feature: / Alarm text (pop-ups and logs)
125030030 | NEL 3 overload 2 | Texts related to feature: / Alarm text (pop-ups and logs)
125030040 | NEL 3 reactive overload | Texts related to feature: / Alarm text (pop-ups and logs)
125030050 | Trip when breaker trips | Texts related to feature: / Parameter name
125037000 | NEL 3 trip changed | Texts related to feature: / Event text (pop-ups, logs and status texts)
125039000 | Non-essential load trip 3 | Texts related to feature: / Assignable function (input/output config menus, Modbus)
126000000 | Low frequency limit | Text related to feature: / Parameter name
126000010 | High frequency limit | Text related to feature: / Parameter name
126000020 | Low voltage limit | Text related to feature: / Parameter name
126000030 | High voltage limit | Text related to feature: / Parameter name
126000040 | Delay | Text related to feature: / Timer text
126001000 | Low frequency limit | Text related to feature: / Parameter name
126001010 | High frequency limit | Text related to feature: / Parameter name
126001020 | Low voltage limit | Text related to feature: / Parameter name
126001030 | High voltage limit | Text related to feature: / Parameter name
126001040 | Delay | Text related to feature: / Timer text
126002000 | P load sharing failure (low frequency) | Text related to feature: / Alarm text (pop-ups and logs)
126002010 | P load sharing failure (high frequency) | Text related to feature: / Alarm text (pop-ups and logs)
126002020 | Q load sharing failure (low voltage) | Text related to feature: / Alarm text (pop-ups and logs)
126002030 | Q load sharing failure (high voltage) | Text related to feature: / Alarm text (pop-ups and logs)
126003000 | P load sharing failure on DG (low frequency) | Text related to feature: / Alarm text (pop-ups and logs)
126003010 | P load sharing failure on DG (high frequency) | Text related to feature: / Alarm text (pop-ups and logs)
126003020 | Q load sharing failure on DG (low voltage) | Text related to feature: / Alarm text (pop-ups and logs)
126003030 | Q load sharing failure on DG (high voltage) | Text related to feature: / Alarm text (pop-ups and logs)
126003040 | Overload on a DG | Text related to feature: / Alarm text (pop-ups and logs)
126003050 | Reverse power on a DG | Text related to feature: / Alarm text (pop-ups and logs)
126003060 | Reactive power export on a DG | Text related to feature: / Alarm text (pop-ups and logs)
126003070 | Reactive power import on a DG | Text related to feature: / Alarm text (pop-ups and logs)
126003080 | Over-current on a DG | Text related to feature: / Alarm text (pop-ups and logs)
126020000 | P load sharing failure (low frequency) | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020001 | P load sharing failure (high frequency) | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020002 | Q load sharing failure (low voltage) | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020003 | Q load sharing failure (high voltage) | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020100 | P load sharing failure on DG (low frequency) | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020101 | P load sharing failure on DG (high frequency) | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020102 | Q load sharing failure on DG (low voltage) | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020103 | Q load sharing failure on DG (high voltage) | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020104 | Overload on a DG | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020105 | Reverse power on a DG | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020106 | Reactive power export on a DG | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020107 | Reactive power import on a DG | Text related to feature: / Assignable function (input/output config menus, Modbus)
126020108 | Over-current on a DG | Text related to feature: / Assignable function (input/output config menus, Modbus)
126100000 | RPM derated power overload 1 | Text related to feature: RPM derate / Alarm text (pop-ups and logs)
126100010 | RPM derated power overload 2 | Text related to feature: RPM derate / Alarm text (pop-ups and logs)
126105000 | RPM derated power overload 1 | Text related to feature: RPM derate / Assignable function (input/output config menus, Modbus)
126105001 | RPM derated power overload 2 | Text related to feature: RPM derate / Assignable function (input/output config menus, Modbus)
126200000 | Connected | Text related to feature: Load reduction / Parameter configuration (selected from a list)
126200001 | AUTO or MANUAL | Text related to feature: Load reduction / Parameter configuration (selected from a list)
126200002 | AUTO | Text related to feature: Load reduction / Parameter configuration (selected from a list)
126200010 | Limit | Text related to feature: Load reduction / Parameter name
126200011 | Enable | Text related to feature: Load reduction / Parameter name
126200012 | Delay | Text related to feature: Load reduction / Parameter name
126200013 | Period time | Text related to feature: Load reduction / Parameter name
126200014 | Pulse time | Text related to feature: Load reduction / Parameter name
126200015 | Power available method | Text related to feature: Load reduction / Parameter name
126219000 | Load reduction output 1 | Text related to feature: Load reduction / Assignable function (input/output config menus, Modbus)
126229000 | Load reduction output 2 | Text related to feature: Load reduction / Assignable function (input/output config menus, Modbus)
130000000 | Emulation active | Texts related to feature: Emulation / Parameter name
130000040 | Emulation disabled (live power) | Texts related to feature: Emulation / Alarm text (pop-ups and logs)
130000050 | Live voltage detected | Texts related to feature: Emulation / Alarm text (pop-ups and logs)
130001000 | Emulation | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130001001 | Emulation not possible on live system | Texts related to feature: Emulation / Event text (pop-ups, logs and status texts)
130001002 | Wire failure L1 | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130001003 | Wire failure L2 | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130001004 | Wire failure L3 | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130001005 | Phase sequence error | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130001006 | Measurement failure | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130001007 | Load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130010000 | Engine | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130010001 | Shaft engine | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130010002 | Shore connection | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130010003 | Inverter | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130010004 | Mains | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130010005 | Mains connection | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130011000 | Start | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130011001 | Stop | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130011002 | Start | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130011003 | Stop | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130012000 | Start failure | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130012010 | Stop failure | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130012020 | Idle speed | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130014000 | Mains voltage | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130014010 | Mains frequency | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130020000 | Governor | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130020001 | Governor mains | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130021000 | GOV auto | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130021001 | GOV manual | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130021002 | GOV up | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130021003 | GOV down | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130021004 | GOV auto | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130021005 | GOV manual | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130021006 | GOV up | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130021007 | GOV down | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130022000 | Droop | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130022010 | Droop | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130023000 | GOV auto | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130023001 | GOV manual | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130023002 | GOV auto | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130023003 | GOV manual | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130030000 | Generator | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130040000 | AVR | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130040001 | AVR mains | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130041000 | AVR auto | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130041001 | AVR manual | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130041002 | AVR up | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130041003 | AVR down | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130041004 | AVR auto | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130041005 | AVR manual | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130041006 | AVR up | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130041007 | AVR down | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130042000 | Loss of excitation | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130042010 | Droop | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130042020 | Over-excitation | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130042030 | Droop | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130043000 | AVR auto | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130043001 | AVR manual | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130043002 | AVR auto | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130043003 | AVR manual | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050000 | Busbar load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050001 | Load on | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050002 | Load off | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050003 | Active load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050004 | Reactive load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050005 | Under-voltage trip | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050006 | Busbar | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050007 | Busbar A | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130050008 | Busbar B | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100000 | Breaker on | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100001 | Breaker off | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100002 | Block open | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100003 | Block close | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100004 | Force open feedback on | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100005 | Force close feedback on | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100006 | Force open feedback off | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100007 | Force close feedback off | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130100008 | Under-voltage coil | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130101000 | Generator breaker | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130102000 | Shaft breaker | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130103000 | Bus tie breaker | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130104000 | Shore breaker | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130105000 | Tie breaker | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
130106000 | Mains breaker | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
131000000 | NEL load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
131000001 | Load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
131000002 | Load on | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
131000003 | Load off | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
131000004 | Active load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
131000005 | Reactive load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
132000000 | Heavy consumer | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
132000001 | Request | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
132000002 | Load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
132000003 | Request | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
132000004 | Load on | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
132000005 | Load off | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
132000006 | Auto connect | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
133000000 | PTI (power take in) load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
133002000 | PTI active load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
133002010 | PTI reactive load | Texts related to feature: Emulation / Real-time user interaction (mainly emulation)
140010000 | Controller status text | Texts related to UI / Assignable function (input/output config menus, Modbus)
140010001 | Controller status text simplified | Texts related to UI / Assignable function (input/output config menus, Modbus)
140110000 | Information | Texts related to UI / Status text (info lines)
140110001 | Warning | Texts related to UI / Status text (info lines)
140120000 | Pop-up text line 1 | Texts related to UI / Assignable function (input/output config menus, Modbus)
140120001 | Pop-up text line 2 | Texts related to UI / Assignable function (input/output config menus, Modbus)
140120002 | Pop-up text line 3 | Texts related to UI / Assignable function (input/output config menus, Modbus)
140120003 | Pop-up text line 4 | Texts related to UI / Assignable function (input/output config menus, Modbus)
140120010 | Pop-up active | Texts related to UI / Assignable function (input/output config menus, Modbus)
140200000 | Activate | Texts related to UI / Timer text
140200010 | Duration | Texts related to UI / Timer text
140200020 | Colour cycle time | Texts related to UI / Timer text
140210000 | Start lamp test | Texts related to UI / Assignable function (input/output config menus, Modbus)
140210001 | Stop lamp test | Texts related to UI / Assignable function (input/output config menus, Modbus)
140220000 | Lamp test started | Texts related to UI / Event text (pop-ups, logs and status texts)
140310000 | Lamp test active | Texts related to UI / Status text (info lines)
140310001 | Press Stop to end lamp test | Texts related to UI / Status text (info lines)
140310002 | Stop | Texts related to UI / Status text (info lines)
140320000 | Local button commands | Texts related to UI / Miscellaneous text (various uses)
147000000 | Controller not part of system | Texts related to system setup (plant) / Alarm text (pop-ups and logs)
147000010 | Active application | Texts related to system setup (plant) / Parameter name
147000020 | Different single-line configurations | Texts related to system setup (plant) / Alarm text (pop-ups and logs)
147000030 | Single-line missing/none active | Texts related to system setup (plant) / Alarm text (pop-ups and logs)
147000040 | Single-line hazard | Texts related to system setup (plant) / Alarm text (pop-ups and logs)
147000050 | Broadcast application | Texts related to system setup (plant) / Parameter name
147000060 | Application to broadcast | Texts related to system setup (plant) / Parameter name
147000070 | ID not present | Texts related to system setup (plant) / Alarm text (pop-ups and logs)
147000080 | Unsupported application | Texts related to system setup (plant) / Alarm text (pop-ups and logs)
147000090 | Application internal CAN protocol conflict | Texts related to system setup (plant) / Alarm text (pop-ups and logs)
147010000 | Controller not part of system | Texts related to system setup (plant) / Assignable function (input/output config menus, Modbus)
147010001 | Different single-line configurations | Texts related to system setup (plant) / Assignable function (input/output config menus, Modbus)
147010002 | Single-line missing/none active | Texts related to system setup (plant) / Assignable function (input/output config menus, Modbus)
147020000 | Application 1 | Texts related to system setup (plant) / Status text (info lines)
147020001 | Application 2 | Texts related to system setup (plant) / Status text (info lines)
147020002 | Application 3 | Texts related to system setup (plant) / Status text (info lines)
147020003 | Application 4 | Texts related to system setup (plant) / Status text (info lines)
147020004 | Off | Texts related to system setup (plant) / Status text (info lines)
147020005 | On | Texts related to system setup (plant) / Status text (info lines)
147020006 | On + activate | Texts related to system setup (plant) / Status text (info lines)
147020007 | Broadcasting application 1 | Texts related to system setup (plant) / Status text (info lines)
147020008 | Broadcasting application 2 | Texts related to system setup (plant) / Status text (info lines)
147020009 | Broadcasting application 3 | Texts related to system setup (plant) / Status text (info lines)
147020010 | Broadcasting application 4 | Texts related to system setup (plant) / Status text (info lines)
147020011 | Broadcast completed | Texts related to system setup (plant) / Status text (info lines)
147020012 | Broadcast aborted | Texts related to system setup (plant) / Status text (info lines)
147050001 | Plant changed: Broadcast | Texts related to system setup (plant) / Event text (pop-ups, logs and status texts)
147050002 | Plant receive complete | Texts related to system setup (plant) / Event text (pop-ups, logs and status texts)
147050003 | Plant receive error | Texts related to system setup (plant) / Event text (pop-ups, logs and status texts)
147050004 | Unit number error | Texts related to system setup (plant) / Event text (pop-ups, logs and status texts)
148000000 | Modbus communication timeout | Texts related to external interfaces (modbus) / Alarm text (pop-ups and logs)
148010000 | Modbus communication timeout | Texts related to external interfaces (modbus) / Assignable function (input/output config menus, Modbus)
149000000 | Application version major | Texts related to software versioning / Label text
149000001 | Application version minor | Texts related to software versioning / Label text
149000002 | Application version micro | Texts related to software versioning / Label text
149000003 | Application version bugfix | Texts related to software versioning / Label text
150000000 | Power management rules network error | Texts related to PMS configuration / Alarm text (pop-ups and logs)
150000020 | Section P> | Texts related to PMS configuration / Parameter name
150000030 | Section P> | Texts related to PMS configuration / Parameter name
150000040 | Section P> factor | Texts related to PMS configuration / Parameter name
150000170 | Mode shift | Texts related to PMS configuration / Parameter name
150000210 | N + X setup | Texts related to PMS configuration / Parameter name
150080031 | Section P> | Texts related to PMS configuration / Alarm text (pop-ups and logs)
150090000 | Calculation in P | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090001 | Calculation in S | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090002 | Power | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090003 | Percent | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090004 | Max. one SC may connect | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090005 | One close command connects corresponding SC | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090006 | One close command connects all SCs | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090007 | Static section | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090008 | Dynamic section | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090009 | All section | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090010 | Normally open | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090011 | Normally closed | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090012 | Run one mains | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090013 | Run all mains | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090014 | N + X OFF | Texts related to PMS configuration / Parameter configuration (selected from a list)
150090030 | N + %s | Texts related to PMS configuration / Parameter configuration (selected from a list)
152000000 | P available limit | Texts related to PMS configuration / Parameter name
152000001 | S available limit | Texts related to PMS configuration / Parameter name
152000002 | Load limit | Texts related to PMS configuration / Parameter name
152000003 | Delay | Texts related to PMS configuration / Timer text
152000004 | Enable | Texts related to PMS configuration / Parameter name
152000005 | Power selection | Texts related to PMS configuration / Parameter name
152000006 | Method | Texts related to PMS configuration / Parameter name
152000007 | Block stop when active | Texts related to PMS configuration / Parameter name
152000010 | Enable | Texts related to PMS configuration / Parameter name
152000011 | Enable | Texts related to PMS configuration / Parameter name
152000012 | Set point | Texts related to PMS configuration / Parameter name
152000013 | Enable | Texts related to PMS configuration / Parameter name
152000014 | Set point | Texts related to PMS configuration / Parameter name
152000015 | Enable | Texts related to PMS configuration / Parameter name
152000016 | Set point | Texts related to PMS configuration / Parameter name
152000017 | Set point | Texts related to PMS configuration / Parameter name
152000018 | Number of gensets to start | Texts related to PMS configuration / Parameter name
152000019 | Multiple shore connections | Texts related to PMS configuration / Parameter name
152000020 | Minimum | Texts related to PMS configuration / Parameter name
152000021 | Minimum delay | Texts related to PMS configuration / Timer text
152000022 | Maximum | Texts related to PMS configuration / Parameter name
152000023 | Maximum delay | Texts related to PMS configuration / Timer text
152000024 | Limit exceeded | Texts related to PMS configuration / Parameter name
152000025 | Switch to equal | Texts related to PMS configuration / Parameter name
152000026 | Adjust set point | Texts related to PMS configuration / Parameter name
152000027 | Protective start | Texts related to PMS configuration / Parameter name
152000028 | kW and kVA | Texts related to PMS configuration / Parameter name
152000029 | kW | Texts related to PMS configuration / Parameter name
152000030 | kVA | Texts related to PMS configuration / Parameter name
152000063 | Auto calculation | Texts related to PMS configuration / Miscellaneous text (various uses)
152000064 | Start %s DG | Texts related to PMS configuration / Miscellaneous text (various uses)
153000000 | Enable | Texts related to PMS configuration / Parameter name
153000001 | Limit | Texts related to PMS configuration / Parameter name
153000002 | Delay | Texts related to PMS configuration / Timer text
153000003 | Multi-start set 1 | Texts related to PMS configuration / Miscellaneous text (various uses)
153000004 | Multi-start set 2 | Texts related to PMS configuration / Miscellaneous text (various uses)
153000005 | No change | Texts related to PMS configuration / Miscellaneous text (various uses)
153120000 | Gensets to start | Texts related to PMS configuration / Miscellaneous text (various uses)
153120020 | Minimum number running | Texts related to PMS configuration / Miscellaneous text (various uses)
153120030 | Prevent load-dependent stop | Texts related to PMS configuration / Miscellaneous text (various uses)
153120040 | Multi-start set 1 | Texts related to PMS configuration / Parameter name
153120050 | Multi-start set 2 | Texts related to PMS configuration / Parameter name
153120060 | Multi-start selection | Texts related to PMS configuration / Parameter name
153120070 | Multi-start set during AMF | Texts related to PMS configuration / Parameter name
160000000 | CODESYS configuration conflict | Texts related to the CODESYS Development System / Alarm text (pop-ups and logs)
160000010 | Startup time | Texts related to the CODESYS Development System / Timer text
160000020 | CODESYS application not OK | Texts related to the CODESYS Development System / Alarm text (pop-ups and logs)
160000030 | Enable | Texts related to the CODESYS Development System / Parameter name
160005000 | CODESYS application OK | Texts related to the CODESYS Development System / Assignable function (input/output config menus, Modbus)
160010000 | CODESYS-add-on | Texts related to the CODESYS Development System / Status text (info lines)
160010001 | CODESYS licence | Texts related to the CODESYS Development System / Status text (info lines)
160010002 | CODESYS runtime environment | Texts related to the CODESYS Development System / Status text (info lines)
160010003 | CODESYS application version | Texts related to the CODESYS Development System / Status text (info lines)
170000000 | ECU Red stop lamp | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000010 | ECU Amber warning lamp | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000020 | ECU Protect lamp | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000030 | ECU Malfunction indicator lamp | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000040 | ECU Communication failure | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000050 | ECU Power configuration | Texts regarding engine communication / Parameter name
170000060 | ECU powerup time | Texts regarding engine communication / Parameter name
170000070 | Enable | Texts regarding engine communication / Parameter name
170000080 | Source address | Texts regarding engine communication / Parameter name
170000090 | Enable | Texts regarding engine communication / Parameter name
170000100 | Source address | Texts regarding engine communication / Parameter name
170000110 | ECU Transmit data suppression | Texts regarding engine communication / Parameter name
170000120 | Source address | Texts regarding engine communication / Parameter name
170000130 | Enable | Texts regarding engine communication / Parameter name
170000140 | Cummins gain | Texts regarding engine communication / Parameter name
170000150 | Scania speed setting | Texts regarding engine communication / Parameter name
170000160 | EIC derate | Texts regarding engine communication / Parameter name
170000170 | ECU Red stop lamp (ECU2) | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000180 | ECU Amber warning lamp (ECU2) | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000190 | ECU Protect lamp (ECU2) | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000200 | ECU Malfunction indicator lamp (ECU2) | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000210 | Escape mode shutdown threshold enable | Texts regarding engine communication / Parameter name
170000220 | Escape mode shutdown threshold | Texts regarding engine communication / Parameter name
170000230 | Escape mode shutdown | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000240 | Use nominal RPM as reference | Texts regarding engine communication / Parameter name
170000250 | RPM nominal value | Texts regarding engine communication / Parameter name
170000260 | frequency nominal value | Texts regarding engine communication / Parameter name
170000270 | Enable | Texts regarding engine communication / Parameter name
170000280 | Low engine oil pressure | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000290 | High engine coolant temperature | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000300 | Engine stop limit exceed | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000310 | Charge 61 | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000320 | Aftertreatment Regeneration Inhibit Switch | Texts regarding engine communication / Parameter name
170000330 | Aftertreatment Regeneration Force Switch | Texts regarding engine communication / Parameter name
170000340 | High Coolant Temperature Lamp - Prewarning | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000350 | High Coolant Temperature Lamp - Warning | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000360 | Low Oil Pressure Lamp - Below operation range | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000370 | High Oil Temperature Lamp - Above operation range | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000380 | Air filter clogging | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000390 | Clogged Fuel Pre-Filter | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000400 | Clogged Fuel Filter | Texts regarding engine communication / Alarm text (pop-ups and logs)
170000410 | Droop settings | Texts regarding engine communication / Parameter name
170000420 | Droop value | Texts regarding engine communication / Parameter name
170000430 | Engine overspeed test command | Texts regarding engine communication / Parameter name
170000440 | Claim all cylinders | Texts regarding engine communication / Parameter name
170000450 | Intermittent oil priming command | Texts regarding engine communication / Parameter name
170000460 | Engine operating mode command | Texts regarding engine communication / Parameter name
170000470 | Engine speed gov parameter command | Texts regarding engine communication / Parameter name
170000480 | Reset trip fuel | Texts regarding engine communication / Parameter name
170000490 | Alternate droop setting | Texts regarding engine communication / Parameter name
170000500 | Speed control | Texts regarding engine communication / Parameter name
170000510 | Rapid start enable | Texts regarding engine communication / Parameter name
170000520 | MTU Speed Demand State | Texts regarding engine communication / Parameter name
170000530 | Local normal switch position | Texts regarding engine communication / Parameter name
170000540 | Local emergency switch position | Texts regarding engine communication / Parameter name
170000550 | Remote normal switch position | Texts regarding engine communication / Parameter name
170000560 | Remote emergency switch position | Texts regarding engine communication / Parameter name
170000580 | Stationary regeneration | Texts regarding engine communication / Parameter name
170000610 | Power off timer | Texts regarding engine communication / Parameter name
170000800 | Auto | Texts regarding engine communication / Parameter configuration (selected from a list)
170000801 | Always ON | Texts regarding engine communication / Parameter configuration (selected from a list)
170000802 | Set with adjustable parameter | Texts regarding engine communication / Parameter configuration (selected from a list)
170000803 | 1500 RPM | Texts regarding engine communication / Parameter configuration (selected from a list)
170000804 | 1800 RPM | Texts regarding engine communication / Parameter configuration (selected from a list)
170000805 | Low idling | Texts regarding engine communication / Parameter configuration (selected from a list)
170000806 | None | Texts regarding engine communication / Parameter configuration (selected from a list)
170000807 | Engine Control Unit (ECU) | Texts regarding engine communication / Parameter configuration (selected from a list)
170000808 | Emulated droop | Texts regarding engine communication / Parameter configuration (selected from a list)
170000809 | Standard J1939 | Texts regarding engine communication / Parameter configuration (selected from a list)
170000810 | Volvo proprietary - Primary speed 50Hz | Texts regarding engine communication / Parameter configuration (selected from a list)
170000811 | Volvo proprietary - Primary speed 60Hz | Texts regarding engine communication / Parameter configuration (selected from a list)
170000812 | Automatic | Texts regarding engine communication / Parameter configuration (selected from a list)
170000813 | Forced | Texts regarding engine communication / Parameter configuration (selected from a list)
170000814 | Database | Texts regarding engine communication / Status text (info lines)
170000815 | Protocol | Texts regarding engine communication / Status text (info lines)
170000816 | Analogue CAN | Texts regarding engine communication / Parameter configuration (selected from a list)
170000817 | Up/Down ECU | Texts regarding engine communication / Parameter configuration (selected from a list)
170000818 | Up/Down CAN | Texts regarding engine communication / Parameter configuration (selected from a list)
170000819 | Analogue ECU | Texts regarding engine communication / Parameter configuration (selected from a list)
170000820 | Analogue ECU relative | Texts regarding engine communication / Parameter configuration (selected from a list)
170000821 | Frequency | Texts regarding engine communication / Parameter configuration (selected from a list)
170000900 | Measurement list filter - available | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000901 | Measurement list filter - clear | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000902 | ECU power | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000903 | Log request (DM2) | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000904 | Log clear (DM2) | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000905 | ECU Communication failure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000906 | ECU Transmit data suppression | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000907 | ECU Speed request suppression | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000908 | Derate | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000909 | Escape mode request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000914 | Enable= | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000915 | Aftertreatment Regeneration Inhibit Switch | Texts regarding engine communication / Parameter name
170000916 | Aftertreatment Regeneration Force Switch | Texts regarding engine communication / Parameter name
170000922 | Speed increase | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000923 | Speed decrease | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000924 | Speed decrease | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000928 | DEF level | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170000930 | ECU reset input | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001000 | Engine speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001001 | Engine coolant temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001002 | Engine oil pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001003 | Engine requested speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001004 | Number of actual faults | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001005 | Engine oil temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001006 | Fuel temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001007 | Boost pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001008 | Air inlet temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001009 | Coolant level | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001010 | Fuel rate | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001011 | Engine intake manifold 1 temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001012 | Drivers demand engine percent torque | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001013 | Actual engine - percent torque | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001014 | Accelerator pedal position | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001015 | Percent load at current speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001016 | Air inlet pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001017 | Exhaust gas temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001018 | Engine hours | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001019 | Engine oil filter differential pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001020 | Battery potential voltage switched | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001021 | Fuel delivery pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001022 | Engine oil level | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001023 | Crankcase pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001024 | Coolant pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001025 | Water in fuel indicator | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001026 | Turbo oil temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001027 | Particulate trap inlet pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001028 | Air filter differential pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001029 | Coolant filter differential pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001030 | Atmospheric pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001031 | Ambient air temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001032 | Exhaust temperature right | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001033 | Exhaust temperature left | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001034 | Engine intercooler temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001035 | Engine trip fuel | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001036 | Engine total fuel used | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001037 | Trip fuel gaseous | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001038 | Total fuel used gaseous | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001039 | Mean trip fuel consumption | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001040 | Nominal power | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001041 | Engine intake manifold 1 absolute pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001042 | Diesel particulate filter lamp command | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001043 | Diesel particulate filter active regeneration inhibited | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001044 | Diesel particulate filter active regeneration status | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001045 | Diesel particulate filter regeneration status | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001046 | Exhaust system high temperature lamp command | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001047 | Air filter differential pressure 2 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001048 | Fuel supply pump inlet pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001049 | Fuel filter (suction side) differential pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001050 | Engine fuel filter differential pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001051 | Engine ECU temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001052 | Exhaust port temperature 01 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001053 | Exhaust port temperature 02 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001054 | Exhaust port temperature 03 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001055 | Exhaust port temperature 04 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001056 | Exhaust port temperature 05 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001057 | Exhaust port temperature 06 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001058 | Exhaust port temperature 07 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001059 | Exhaust port temperature 08 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001060 | Exhaust port temperature 09 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001061 | Exhaust port temperature 10 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001062 | Exhaust port temperature 11 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001063 | Exhaust port temperature 12 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001064 | Exhaust port temperature 13 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001065 | Exhaust port temperature 14 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001066 | Exhaust port temperature 15 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001067 | Exhaust port temperature 16 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001068 | Exhaust port temperature 17 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001069 | Exhaust port temperature 18 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001070 | Exhaust port temperature 19 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001071 | Exhaust port temperature 20 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001072 | Engine filtered fuel delivery pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001073 | Engine coolant temperature 2 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001074 | Engine coolant temperature 3 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001075 | Engine coolant pump outlet temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001076 | Engine auxiliary coolant temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001077 | Engine turbocharger 1 turbine intake temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001078 | Engine turbocharger 2 turbine intake temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001079 | Engine auxiliary coolant pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001080 | Ambient conditions 2 specific humidity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001081 | Engine turbocharger 2 speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001082 | Engine turbocharger 3 speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001083 | Trip engine running time | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001084 | Trip idle time | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001085 | Engine turbocharger 1 speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001086 | Nominal friction - percent torque | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001087 | Engines desired operating speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001088 | Engine intake manifold 2 temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001089 | Aftertreatment 1 diesel exhaust fluid tank level | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001090 | Aftertreatment 1 diesel exhaust fluid tank temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001091 | Aftertreatment 1 intake NOx | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001092 | Aftertreatment 1 outlet NOx | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001093 | Aftertreatment 1 DEF actual dosing quantity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001094 | Aftertreatment 1 DEF doser absolute pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001095 | Aftertreatment 1 SCR dosing air assist valve | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001096 | Aftertreatment 1 DEF dosing requested quantity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001097 | Aftertreatment 1 SCR catalyst intake gas temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001098 | Aftertreatment 1 SCR catalyst outlet gas temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001099 | Aftertreatment 2 intake NOx | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001100 | Aftertreatment 2 outlet NOx | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001101 | Aftertreatment 2 DEF actual dosing quantity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001102 | Aftertreatment 2 DEF dosing absolute pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001103 | Aftertreatment 2 SCR dosing air assist valve | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001104 | Aftertreatment 2 DEF dosing requested quantity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001105 | Aftertreatment 2 SCR catalyst intake gas temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001106 | Aftertreatment 2 SCR catalyst outlet gas temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001107 | Engine oil-filter outlet pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001108 | Engine operating state | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001109 | Source address of controlling device | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001110 | Engine rated speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001111 | Engine speed at idle point 1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001112 | ECU identification information | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001113 | Aftertreatment SCR operator inducement severity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001114 | Aftertreatment SCR operator inducement active | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001115 | Aftertreatment 1 DPF outlet gas temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001116 | Aftertreatment 1 DPF time to next active regeneration | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001117 | Engine charge air cooler 1 outlet temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001118 | Diesel particulate filter 1 soot load percent | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001119 | Aftertreatment 1 DEF average consumption | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001120 | Engine operating derate request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001121 | SW identification | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001122 | Engine demand - percent torque | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001123 | Aftertreatment 1 intake percent oxygen 1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001124 | Aftertreatment 1 outlet percent oxygen 1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001125 | Engine throttle actuator 1 control command | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001126 | Long-term fuel trim | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001127 | Short-term fuel trim | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001128 | Engine exhaust gas oxygen sensor closed loop operation | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001129 | Engine desired ignition timing no 1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001130 | Engine actual ignition timing | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001131 | Engine amber warning lamp command | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001132 | Engine red stop lamp command | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001133 | Time left to torque reduction | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001134 | SCR Inducement severity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001135 | SCR Inducement reason | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001136 | Time left to severe torque reduction | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001137 | Preheat feedback | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001138 | Start request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001139 | Stop request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001140 | Govenor mode request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001141 | Idle speed select | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001142 | Frequency select | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001143 | Diagnosis request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001144 | Preheat request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001145 | Engine protection override | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001146 | Accelerator pedal position | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001147 | Accelerator pedal position | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001148 | Fuel disable request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001149 | Engine Stop Request | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001150 | Engine Starter Mode | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001151 | Actual Maximum Available Engine - Percent Torque | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001152 | Engine Coolant Pre-heated State | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001153 | Engine Shutdown Override Switch | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001154 | Engine Intake Manifold 3 Temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001155 | Engine Intake Manifold 4 Temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001156 | Engine Oil Filter Intake Pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001157 | Engine Turbocharger 2 Boost Pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001158 | Engine Fuel 1 Injector Metering Rail 1 Pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001159 | Battery Potential / Power Input 1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001160 | Aftertreatment 1 Exhaust Temperature 1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001161 | Wheel-Based Vehicle Speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001162 | Aftertreatment 1 Exhaust Gas Mass Flow Rate | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001163 | Aftertreatment 1 Diesel Particulate Filter Differential Pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001164 | Aftertreatment 1 Diesel Oxidation Catalyst Intake Temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001165 | Aftertreatment 1 Diesel Particulate Filter Intake Temperature | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001166 | Diesel Particulate Filter Active Regeneration Inhibited Due to Out of Neutral | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001167 | Diesel Particulate Filter Active Regeneration Inhibited Due to Parking Brake Not Set | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001168 | Operator Inducement Time to Torque Derate Level 1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001169 | Operator Inducement Time to Torque Derate Level 2 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001170 | Transmission Neutral Switch | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001171 | Parking Brake Switch | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001172 | Brake Switch | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001173 | Alternator 1 Status | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001174 | Engine Oil Viscosity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001175 | Engine Oil Density | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001176 | Engine Oil Relative Dielectricity (High Resolution) | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001177 | Engine Fuel Dynamic Viscosity | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001178 | Engine Fuel Density | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001179 | Engine Fuel Dielectricity (High Resolution) | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001180 | Engine Fuel 1 Temperature 1 (High Resolution) | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001181 | Engine Oil Filter Differential Pressure (Extended Range) | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001182 | Engine Air Filter 3 Differential Pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001183 | Engine Air Filter 4 Differential Pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001184 | Engine Throttle Valve 1 Position 1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001185 | Engine Fuel Valve 1 Intake Absolute Pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001186 | Engine Turbocharger 1 Boost Pressure | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001187 | Engine Cylinder 1 Ignition Timing | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001188 | Engine Intake Air Mass Flow Rate | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001189 | Aftertreatment 1 Diesel Particulate Filter Ash Load Percent | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001190 | Engine Fan 1 Estimated Percent Speed | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001191 | Battery Charger 1 Output Voltage | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001192 | Battery Charger 1 Output Current | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001193 | Red lamp from ECU1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001194 | Amber lamp from ECU1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001195 | Protect lamp from ECU1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001196 | Malfunction lamp from ECU1 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001197 | Red lamp from ECU2 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001198 | Amber lamp from ECU2 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001199 | Protect lamp from ECU2 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001200 | Malfunction lamp from ECU2 | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001201 | Number of activations of EIO | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001202 | Accumulated EIO time | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001203 | Time left of EIO Operation | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001204 | Cummins Governing | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001875 | ECU ID | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
170001876 | ECU Status | Texts regarding engine communication / Assignable function (input/output config menus, Modbus)
180000000 | Selection | Texts regarding Fieldbus / Parameter name
180000010 | Selection | Texts regarding Fieldbus / Parameter name
180000100 | Not locked | Texts regarding Fieldbus / Parameter name
180000110 | Locked to ext. rack | Texts regarding Fieldbus / Parameter name
180000120 | Locked to position | Texts regarding Fieldbus / Parameter name
180000130 | Locked to module | Texts regarding Fieldbus / Parameter name
181000000 | Fieldbus conflict | Texts regarding Fieldbus / Alarm text (pop-ups and logs)
181000010 | Fieldbus connection missing | Texts regarding Fieldbus / Alarm text (pop-ups and logs)
182000000 | Fieldbus conflict | Texts regarding Fieldbus / Assignable function (input/output config menus, Modbus)
182000001 | Fieldbus connection missing | Texts regarding Fieldbus / Assignable function (input/output config menus, Modbus)
183000000 | Fieldbus configuration: Status OK | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000010 | Fieldbus configuration: Could not resolve fieldbus | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000020 | Fieldbus configuration: Ext. rack added | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000030 | Fieldbus configuration: Ext. rack missing | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000040 | Fieldbus configuration: Ext. rack moved | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000050 | Fieldbus configuration: Ext. rack replaced | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000060 | Fieldbus configuration: Ext. rack modified | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000070 | Fieldbus configuration: Module added | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000080 | Fieldbus configuration: Module missing | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000090 | Fieldbus configuration: Module moved - Same type | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000100 | Fieldbus configuration: Module moved - Different type | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000110 | Fieldbus configuration: Module replaced - Same type | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000120 | Fieldbus configuration: Module replaced - Different type | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000130 | Fieldbus configuration: Connection added | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000140 | Fieldbus configuration: Connection missing | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000150 | Fieldbus configuration: Status not set | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000160 | Fieldbus configuration: Ext. rack update in progress | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000170 | Fieldbus configuration: Ext. rack not supported | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
183000180 | Fieldbus configuration: Module not supported | Texts regarding Fieldbus / Event text (pop-ups, logs and status texts)
184000000 | Fieldbus change detected | Texts regarding Fieldbus / Label text
184000001 | Use PICUS fieldbus supervision to verify configuration. | Texts regarding Fieldbus / Label text
184000002 | Minor changes were made | Texts regarding Fieldbus / Label text
184000003 | Select Save to solve conflicts | Texts regarding Fieldbus / Label text
184000010 | OK | Texts regarding Fieldbus / Label text
184000011 | Save | Texts regarding Fieldbus / Label text
184000012 | Cancel | Texts regarding Fieldbus / Label text
190000000 | Generator primary VT | Texts regarding digital AVR / Miscellaneous text (various uses)
190000010 | Generator secondary VT | Texts regarding digital AVR / Miscellaneous text (various uses)
190000020 | Busbar primary VT | Texts regarding digital AVR / Miscellaneous text (various uses)
190000030 | Busbar secondary VT | Texts regarding digital AVR / Miscellaneous text (various uses)
190000040 | Enable VT | Texts regarding digital AVR / Miscellaneous text (various uses)
190000050 | Start on threshold PWM | Texts regarding digital AVR / Miscellaneous text (various uses)
190000060 | Start on threshold activation | Texts regarding digital AVR / Miscellaneous text (various uses)
190000070 | Soft-start ramp | Texts regarding digital AVR / Miscellaneous text (various uses)
190000080 | Knee set point | Texts regarding digital AVR / Miscellaneous text (various uses)
190000090 | U/f variable slope | Texts regarding digital AVR / Miscellaneous text (various uses)
190000100 | Soft voltage recovery | Texts regarding digital AVR / Miscellaneous text (various uses)
190000110 | Adjust LAM | Texts regarding digital AVR / Miscellaneous text (various uses)
190000120 | Reactive droop compensation | Texts regarding digital AVR / Miscellaneous text (various uses)
190000130 | Voltage droop compensation | Texts regarding digital AVR / Miscellaneous text (various uses)
190000140 | Droop type | Texts regarding digital AVR / Miscellaneous text (various uses)
190000150 | Excitation reference for dry alternator | Texts regarding digital AVR / Miscellaneous text (various uses)
190000160 | Current limitation transformer | Texts regarding digital AVR / Miscellaneous text (various uses)
190000170 | Current limitation induction motor | Texts regarding digital AVR / Miscellaneous text (various uses)
190000180 | Current limitation type | Texts regarding digital AVR / Miscellaneous text (various uses)
190000190 | PID gain factor | Texts regarding digital AVR / Miscellaneous text (various uses)
190000200 | PID RMS enable (Average/RMS) | Texts regarding digital AVR / Miscellaneous text (various uses)
190000210 | Write all settings | Texts regarding digital AVR / Miscellaneous text (various uses)
190000220 | Bias scale | Texts regarding digital AVR / Miscellaneous text (various uses)
190000230 | Controls | Texts regarding digital AVR / Miscellaneous text (various uses)
190000240 | Analogue bias input type | Texts regarding digital AVR / Miscellaneous text (various uses)
190000250 | AC configuration | Texts regarding digital AVR / Miscellaneous text (various uses)
190000260 | Minimum frequency threshold | Texts regarding digital AVR / Miscellaneous text (various uses)
190000270 | Minimum VBus threshold | Texts regarding digital AVR / Miscellaneous text (various uses)
190000280 | SVR and LAM configuration | Texts regarding digital AVR / Miscellaneous text (various uses)
190000290 | LAM duration | Texts regarding digital AVR / Miscellaneous text (various uses)
190000300 | Reset all DVC alarms | Texts regarding digital AVR / Miscellaneous text (various uses)
190000310 | Regulation selection | Texts regarding digital AVR / Miscellaneous text (various uses)
190000320 | Power-up time | Texts regarding digital AVR / Timer text
190000330 | Digital AVR modes | Texts regarding digital AVR / Miscellaneous text (various uses)
191000020 | Digital AVR communication error | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000030 | Dry mode: Voltage level unexpected | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000040 | Over-voltage | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000050 | Under-voltage | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000060 | Over-frequency | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000070 | Under-frequency | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000080 | Open diode | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000090 | Shorted diode | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000100 | Reverse kW | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000110 | Reverse kvar | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000120 | Pt100 1 alarm | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000130 | Pt100 1 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000140 | Pt100 2 alarm | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000150 | Pt100 2 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000160 | Pt100 3 alarm | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000170 | Pt100 3 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000180 | Pt100 4 alarm | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000190 | Pt100 4 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000200 | Pt100 5 alarm | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000210 | Pt100 5 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000220 | PTC 1 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000230 | PTC 2 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000240 | PTC 3 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000250 | PTC 4 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000260 | PTC 5 fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000270 | Sensing lost | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000280 | Unbalanced voltage | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000290 | Unbalanced current | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000300 | Short circuit | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000310 | IGBT overheat | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000320 | Motor start | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000330 | PWR bridge overload | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000340 | Power supply | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000350 | CAN supply | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000360 | Pt100 1 open short fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000370 | Pt100 2 open short fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000380 | Pt100 3 open short fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000390 | Pt100 4 open short fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000400 | Pt100 5 open short fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000410 | AIN 1 wire break fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000420 | AIN 2 wire break fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000430 | AIN 3 wire break fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000440 | AIN 4 wire break fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000450 | AOUT 1 overload wire break fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000460 | AOUT 2 overload wire break fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000470 | AOUT 3 overload wire break fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000480 | AOUT 4 overload wire break fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000490 | DOUT overload fault status | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000500 | Phase rotation direction fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000510 | Stator over-current U | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000520 | Stator over-current V | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000530 | Stator over-current W | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000540 | Exceeding active power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000550 | Exceeding U active power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000560 | Exceeding V active power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000570 | Exceeding W active power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000580 | I2T stator fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000590 | Apparent power fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000600 | Exceeding U apparent power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000610 | Exceeding V apparent power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000620 | Exceeding W apparent power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000630 | Reactive power fault | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000640 | Exceeding U reactive power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000650 | Exceeding V reactive power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000660 | Exceeding W reactive power | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000670 | DAVR unsupported AC configuration | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000680 | Illegal DAVR configuration | Texts regarding digital AVR / Alarm text (pop-ups and logs)
191000690 | Invalid DAVR configuration | Texts regarding digital AVR / Alarm text (pop-ups and logs)
192000000 | Reg mode status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000001 | V/Hz limit status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000002 | Stator current limit status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000003 | Soft-start ramp status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000004 | Set point high limit AVR status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000005 | Set point low limit AVR status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000006 | Set point high limit volt matching status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000007 | Set point low limit volt matching status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000008 | Set point high limit FCR status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000009 | Set point low limit FCR status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000010 | Set point high limit var status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000011 | Set point low limit var status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000012 | Set point high limit PF gen status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000013 | Set point low limit PF gen status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000014 | Set point high limit PF grid status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000015 | Set point low limit PF grid status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000016 | Start and threshold status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000017 | Engine help status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000018 | Motor start status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000019 | Over-voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000020 | Under-voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000021 | Over-frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000022 | Under-frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000023 | Over-frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000024 | Under-frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000025 | Reverse kW | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000026 | Reverse kvar | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000027 | Pt100 1 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000028 | Pt100 1 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000029 | Pt100 2 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000030 | Pt100 2 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000031 | Pt100 3 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000032 | Pt100 3 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000033 | Pt100 4 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000034 | Pt100 4 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000035 | Pt100 5 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000036 | Pt100 5 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000037 | PTC 1 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000038 | PTC 2 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000039 | PTC 3 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000040 | PTC 4 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000041 | PTC 5 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000042 | Sensing lost | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000043 | Unbalanced voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000044 | Unbalanced current | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000045 | Short circuit | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000046 | IGBT overheat | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000047 | Motor start | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000048 | PWR bridge overload | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000049 | Power supply | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000050 | CAN supply | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000051 | Pt100 1 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000052 | Pt100 2 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000053 | Pt100 3 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000054 | Pt100 4 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000055 | Pt100 5 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000056 | AIN 1 wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000057 | AIN 2 wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000058 | AIN 3 wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000059 | AIN 4 wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000060 | AOUT 1 overload wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000061 | AOUT 2 overload wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000062 | AOUT 3 overload wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000063 | AOUT 4 overload wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000064 | DOUT overload fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000065 | Pt100-1 | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000066 | Pt100-2 | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000067 | Pt100-3 | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000068 | Pt100-4 | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000069 | Pt100-5 | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000070 | Generator excitation field voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000071 | Generator excitation field current | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000072 | Generator average line-line AC RMS voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000073 | Generator average line-neutral AC RMS voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000074 | Generator average AC frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000075 | Generator average AC RMS current | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000076 | Generator total reactive power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000077 | Generator overall power factor | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000078 | Generator overall power factor lagging | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000079 | Generator total active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000080 | Generator total apparent power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000081 | Phase rotation | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000082 | Current U stator | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000083 | Current V stator | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000084 | Current W stator | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000085 | Exceeding active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000086 | Exceeding U active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000087 | Exceeding V active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000088 | Exceeding W active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000089 | I2T | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000090 | Exceeding apparent power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000091 | Exceeding U apparent power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000092 | Exceeding V apparent power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000093 | Exceeding W apparent power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000094 | Exceeding reactive power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000095 | Exceeding U reactive power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000096 | Exceeding V reactive power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000097 | Exceeding W reactive power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000098 | Customer ID | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000099 | Firmware version | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000100 | Firmware sub-version | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000101 | Firmware build | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000102 | USB LED | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000103 | Volt match LED | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000104 | PF kvar LED | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000105 | IEXC LED | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000106 | Fault diode LED | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000107 | Fault EXC LED | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000108 | Fault volt LED | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000109 | Fault freq LED | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000110 | RTD1 type | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000111 | RTD2 type | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000112 | RTD3 type | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000113 | RTD4 type | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000114 | RTD5 type | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000115 | PSS function active | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000116 | PSS password status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000117 | Customer ID DVC350 | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192000118 | AVR model | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500000 | Over-voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500001 | Under-voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500002 | Over-frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500003 | Under-frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500004 | Over-frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500005 | Under-frequency | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500006 | Reverse kW | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500007 | Reverse kvar | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500008 | Pt100 1 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500009 | Pt100 1 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500010 | Pt100 2 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500011 | Pt100 2 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500012 | Pt100 3 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500013 | Pt100 3 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500014 | Pt100 4 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500015 | Pt100 4 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500016 | Pt100 5 alarm | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500017 | Pt100 5 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500018 | PTC 1 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500019 | PTC 2 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500020 | PTC 3 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500021 | PTC 4 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500022 | PTC 5 fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500023 | Sensing lost | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500024 | Unbalanced voltage | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500025 | Unbalanced current | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500026 | Short circuit | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500027 | IGBT overheat | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500028 | Motor start | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500029 | PWR bridge overload | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500030 | Power supply | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500031 | CAN supply | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500032 | Pt100 1 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500033 | Pt100 2 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500034 | Pt100 3 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500035 | Pt100 4 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500036 | Pt100 5 open short fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500037 | AIN 1 wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500038 | AIN 2 wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500039 | AIN 3 wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500040 | AIN 4 wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500041 | AOUT 1 overload wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500042 | AOUT 2 overload wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500043 | AOUT 3 overload wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500044 | AOUT 4 overload wire break fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500045 | DOUT overload fault status | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500046 | Phase rotation direction fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500047 | Stator over-current U | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500048 | Stator over-current V | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500049 | Stator over-current W | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500050 | Exceeding active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500051 | Exceeding U active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500052 | Exceeding V active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500053 | Exceeding W active power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500054 | I2T stator fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500055 | Apparent power fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500056 | Exceeding U apparent power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500057 | Exceeding V apparent power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500058 | Exceeding W apparent power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500059 | Reactive power fault | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500060 | Exceeding U reactive power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500061 | Exceeding V reactive power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500062 | Exceeding W reactive power | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
192500063 | Communication failure | Texts regarding digital AVR / Assignable function (input/output config menus, Modbus)
194000000 | Use the controller AC settings | Texts regarding digital AVR / Label text
194000001 | 2-phase (W-U) | Texts regarding digital AVR / Label text
194000002 | 2-phase (V-W) | Texts regarding digital AVR / Label text
194000003 | 3-phase (U-V-W) | Texts regarding digital AVR / Label text
194000004 | SVR | Texts regarding digital AVR / Label text
194000005 | SVR + LAM | Texts regarding digital AVR / Label text
194000006 | Reactive droop compensation | Texts regarding digital AVR / Label text
194000007 | Voltage line droop compensation | Texts regarding digital AVR / Label text
194000008 | Magnetisation | Texts regarding digital AVR / Label text
194000009 | Inductive motor | Texts regarding digital AVR / Label text
194000010 | 4 to 20 mA | Texts regarding digital AVR / Label text
194000011 | +- 10 V | Texts regarding digital AVR / Label text
194000012 | 0 to 10 V | Texts regarding digital AVR / Label text
194000013 | Potentiometer | Texts regarding digital AVR / Label text
194000014 | Communication error | Texts regarding digital AVR / Label text
194000015 | +- 5 V | Texts regarding digital AVR / Label text
194000016 | CAN bias | Texts regarding digital AVR / Label text
194000017 | Dry alternator | Texts regarding digital AVR / Label text
194000018 | Ventilation mode | Texts regarding digital AVR / Label text
194500000 | Reg mode status | Texts regarding digital AVR / Label text
194500001 | V/Hz limit status | Texts regarding digital AVR / Label text
194500002 | Stator current limit status | Texts regarding digital AVR / Label text
194500003 | Soft-start ramp status | Texts regarding digital AVR / Label text
194500004 | Set point high limit AVR status | Texts regarding digital AVR / Label text
194500005 | Set point low limit AVR status | Texts regarding digital AVR / Label text
194500006 | Set point high limit volt matching status | Texts regarding digital AVR / Label text
194500007 | Set point low limit volt matching status | Texts regarding digital AVR / Label text
194500008 | Set point high limit FCR status | Texts regarding digital AVR / Label text
194500009 | Set point low limit FCR status | Texts regarding digital AVR / Label text
194500010 | Set point high limit var status | Texts regarding digital AVR / Label text
194500011 | Set point low limit var status | Texts regarding digital AVR / Label text
194500012 | Set point high limit PF gen status | Texts regarding digital AVR / Label text
194500013 | Set point low limit PF gen status | Texts regarding digital AVR / Label text
194500014 | Set point high limit PF grid status | Texts regarding digital AVR / Label text
194500015 | Set point low limit PF grid status | Texts regarding digital AVR / Label text
194500016 | Start and threshold status | Texts regarding digital AVR / Label text
194500017 | Engine help status | Texts regarding digital AVR / Label text
194500018 | Motor start status | Texts regarding digital AVR / Label text
194500019 | Over-voltage | Texts regarding digital AVR / Label text
194500020 | Under-voltage | Texts regarding digital AVR / Label text
194500021 | Over-frequency | Texts regarding digital AVR / Label text
194500022 | Under-frequency | Texts regarding digital AVR / Label text
194500023 | Over-frequency | Texts regarding digital AVR / Label text
194500024 | Under-frequency | Texts regarding digital AVR / Label text
194500025 | Reverse kW | Texts regarding digital AVR / Label text
194500026 | Reverse kvar | Texts regarding digital AVR / Label text
194500027 | Pt100 1 alarm | Texts regarding digital AVR / Label text
194500028 | Pt100 1 fault | Texts regarding digital AVR / Label text
194500029 | Pt100 2 alarm | Texts regarding digital AVR / Label text
194500030 | Pt100 2 fault | Texts regarding digital AVR / Label text
194500031 | Pt100 3 alarm | Texts regarding digital AVR / Label text
194500032 | Pt100 3 fault | Texts regarding digital AVR / Label text
194500033 | Pt100 4 alarm | Texts regarding digital AVR / Label text
194500034 | Pt100 4 fault | Texts regarding digital AVR / Label text
194500035 | Pt100 5 alarm | Texts regarding digital AVR / Label text
194500036 | Pt100 5 fault | Texts regarding digital AVR / Label text
194500037 | PTC 1 fault | Texts regarding digital AVR / Label text
194500038 | PTC 2 fault | Texts regarding digital AVR / Label text
194500039 | PTC 3 fault | Texts regarding digital AVR / Label text
194500040 | PTC 4 fault | Texts regarding digital AVR / Label text
194500041 | PTC 5 fault | Texts regarding digital AVR / Label text
194500042 | Sensing lost | Texts regarding digital AVR / Label text
194500043 | Unbalanced voltage | Texts regarding digital AVR / Label text
194500044 | Unbalanced current | Texts regarding digital AVR / Label text
194500045 | Short circuit | Texts regarding digital AVR / Label text
194500046 | IGBT overheat | Texts regarding digital AVR / Label text
194500047 | Motor start | Texts regarding digital AVR / Label text
194500048 | PWR bridge overload | Texts regarding digital AVR / Label text
194500049 | Power supply | Texts regarding digital AVR / Label text
194500050 | CAN supply | Texts regarding digital AVR / Label text
194500051 | Pt100 1 open short fault status | Texts regarding digital AVR / Label text
194500052 | Pt100 2 open short fault status | Texts regarding digital AVR / Label text
194500053 | Pt100 3 open short fault status | Texts regarding digital AVR / Label text
194500054 | Pt100 4 open short fault status | Texts regarding digital AVR / Label text
194500055 | Pt100 5 open short fault status | Texts regarding digital AVR / Label text
194500056 | AIN 1 wire break fault status | Texts regarding digital AVR / Label text
194500057 | AIN 2 wire break fault status | Texts regarding digital AVR / Label text
194500058 | AIN 3 wire break fault status | Texts regarding digital AVR / Label text
194500059 | AIN 4 wire break fault status | Texts regarding digital AVR / Label text
194500060 | AOUT 1 overload wire break fault status | Texts regarding digital AVR / Label text
194500061 | AOUT 2 overload wire break fault status | Texts regarding digital AVR / Label text
194500062 | AOUT 3 overload wire break fault status | Texts regarding digital AVR / Label text
194500063 | AOUT 4 overload wire break fault status | Texts regarding digital AVR / Label text
194500064 | DOUT overload fault status | Texts regarding digital AVR / Label text
194500065 | Pt100-1 | Texts regarding digital AVR / Label text
194500066 | Pt100-2 | Texts regarding digital AVR / Label text
194500067 | Pt100-3 | Texts regarding digital AVR / Label text
194500068 | Pt100-4 | Texts regarding digital AVR / Label text
194500069 | Pt100-5 | Texts regarding digital AVR / Label text
194500070 | Generator excitation field voltage | Texts regarding digital AVR / Label text
194500071 | Generator excitation field current | Texts regarding digital AVR / Label text
194500072 | Generator average line-line AC RMS voltage | Texts regarding digital AVR / Label text
194500073 | Generator average line-neutral AC RMS voltage | Texts regarding digital AVR / Label text
194500074 | Generator average AC frequency | Texts regarding digital AVR / Label text
194500075 | Generator average AC RMS current | Texts regarding digital AVR / Label text
194500076 | Generator total reactive power | Texts regarding digital AVR / Label text
194500077 | Generator overall power factor | Texts regarding digital AVR / Label text
194500078 | Generator overall power factor lagging | Texts regarding digital AVR / Label text
194500079 | Generator total active power | Texts regarding digital AVR / Label text
194500080 | Generator total apparent power | Texts regarding digital AVR / Label text
194500081 | Request status | Texts regarding digital AVR / Label text
194500082 | Request value | Texts regarding digital AVR / Label text
194500083 | Phase rotation | Texts regarding digital AVR / Label text
194500084 | Current U stator | Texts regarding digital AVR / Label text
194500085 | Current V stator | Texts regarding digital AVR / Label text
194500086 | Current W stator | Texts regarding digital AVR / Label text
194500087 | Exceeding active power | Texts regarding digital AVR / Label text
194500088 | Exceeding U active power | Texts regarding digital AVR / Label text
194500089 | Exceeding V active power | Texts regarding digital AVR / Label text
194500090 | Exceeding W active power | Texts regarding digital AVR / Label text
194500091 | I2T | Texts regarding digital AVR / Label text
194500092 | Exceeding apparent power | Texts regarding digital AVR / Label text
194500093 | Exceeding U apparent power | Texts regarding digital AVR / Label text
194500094 | Exceeding V apparent power | Texts regarding digital AVR / Label text
194500095 | Exceeding W apparent power | Texts regarding digital AVR / Label text
194500096 | Exceeding reactive power | Texts regarding digital AVR / Label text
194500097 | Exceeding U reactive power | Texts regarding digital AVR / Label text
194500098 | Exceeding V reactive power | Texts regarding digital AVR / Label text
194500099 | Exceeding W reactive power | Texts regarding digital AVR / Label text
200000000 | Digital custom alarm | Texts related to system behaviour / Alarm text (pop-ups and logs)
200009000 | Digital custom alarm | Texts related to system behaviour / Assignable function (input/output config menus, Modbus)
200009001 | Digital custom alarm | Texts related to system behaviour / Assignable function (input/output config menus, Modbus)
200010000 | Analogue custom alarm | Texts related to system behaviour / Alarm text (pop-ups and logs)
200019000 | Analogue custom alarm | Texts related to system behaviour / Assignable function (input/output config menus, Modbus)
200019001 | Analogue custom alarm | Texts related to system behaviour / Assignable function (input/output config menus, Modbus)
200020000 | Controller rack | Texts related to system behaviour / Label text
200021000 | Extension rack | Texts related to system behaviour / Label text
200021101 | Engine Control Unit | Texts related to system behaviour / Label text
200021401 | DEIF DVC 550 | Texts related to system behaviour / Label text
200021403 | DEIF DVC 350 | Texts related to system behaviour / Label text
200021405 | Leroy Somer D550 | Texts related to system behaviour / Label text
200021407 | Leroy Somer D350 | Texts related to system behaviour / Label text
200030000 | Set point | Texts related to system behaviour / Parameter name
200030002 | Delay | Texts related to system behaviour / Parameter name
200030003 | Action | Texts related to system behaviour / Parameter name
200030004 | Inhibit | Texts related to system behaviour / Parameter name
200030005 | Configuration | Texts related to system behaviour / Parameter name
200030006 | UTC shelved | Texts related to system behaviour / Parameter name
200030007 | Enable | Texts related to system behaviour / Parameter name
200030008 | Trigger level | Texts related to system behaviour / Parameter name
200030009 | Low | Texts related to system behaviour / Parameter name
200030010 | High | Texts related to system behaviour / Parameter name
200030011 | Auto acknowledge | Texts related to system behaviour / Parameter name
200030012 | Latch | Texts related to system behaviour / Parameter name
200030013 | Shelved | Texts related to system behaviour / Parameter name
200030014 | Out of service | Texts related to system behaviour / Parameter name
200030016 | Reset hysteresis | Texts related to system behaviour / Parameter name
200030017 | Suppress action | Texts related to system behaviour / Parameter name
200030018 | Actual value | Texts related to system behaviour / Parameter name
200030019 | Timer remaining | Texts related to system behaviour / Parameter name
200030020 | Counter | Texts related to system behaviour / Parameter name
200030021 | State | Texts related to system behaviour / Parameter name
200030022 | Test state | Texts related to system behaviour / Parameter name
200030023 | No alarm | Texts related to system behaviour / Parameter name
200030024 | Unacknowledged | Texts related to system behaviour / Parameter name
200030025 | Acknowledged | Texts related to system behaviour / Parameter name
200030026 | Unacknowledged (Return to normal) | Texts related to system behaviour / Parameter name
200030027 | Unacknowledged latched | Texts related to system behaviour / Parameter name
200030028 | Acknowledged latched | Texts related to system behaviour / Parameter name
200030029 | Shelved | Texts related to system behaviour / Parameter name
200030030 | Out of service | Texts related to system behaviour / Parameter name
200030031 | Latched | Texts related to system behaviour / Parameter name
200030032 | Active | Texts related to system behaviour / Parameter name
200030033 | Inhibited | Texts related to system behaviour / Parameter name
200030040 | Tripped value | Texts related to system behaviour / Parameter name
200030041 | Shelved time | Texts related to system behaviour / Parameter name
200030042 | Severity | Texts related to system behaviour / Parameter name
200030100 | Digital output alarms | Texts related to system behaviour / Parameter name
200030101 | Digital input functions | Texts related to system behaviour / Parameter name
200030102 | Digital output functions | Texts related to system behaviour / Parameter name
200030103 | Analogue input functions | Texts related to system behaviour / Parameter name
200030104 | Analogue output functions | Texts related to system behaviour / Parameter name
200030105 | Measurement groups | Texts related to system behaviour / Parameter name
200040000 | Translations | Texts related to system behaviour / Label text
200040001 | Parameters | Texts related to system behaviour / Label text
200040002 | Input/output configuration | Texts related to system behaviour / Label text
200040003 | Permissions | Texts related to system behaviour / Label text
200040004 | Live data | Texts related to system behaviour / Label text
200040005 | Alarm acknowledge | Texts related to system behaviour / Label text
200040006 | Alarm reset latch | Texts related to system behaviour / Label text
200040007 | Alarm out of service | Texts related to system behaviour / Label text
200040008 | Alarm shelved | Texts related to system behaviour / Label text
200040009 | Log | Texts related to system behaviour / Label text
200040010 | Communication | Texts related to system behaviour / Label text
200040011 | Firmware | Texts related to system behaviour / Label text
200040012 | Date and time | Texts related to system behaviour / Label text
200040013 | Report | Texts related to system behaviour / Label text
200040014 | CustomLogic | Texts related to system behaviour / Label text
200040015 | Single-line supervision | Texts related to system behaviour / Label text
200040016 | Single-line creator | Texts related to system behaviour / Label text
200040017 | Emulation | Texts related to system behaviour / Label text
200040018 | Backup and restore | Texts related to system behaviour / Label text
200040019 | Change controller | Texts related to system behaviour / Label text
200040020 | Counters | Texts related to system behaviour / Label text
200040021 | View design | Texts related to system behaviour / Label text
200040022 | Regulator status | Texts related to system behaviour / Label text
200040023 | Quick connect | Texts related to system behaviour / Label text
200040024 | Backup | Texts related to system behaviour / Label text
200040025 | Restore | Texts related to system behaviour / Label text
200040026 | Alarm test | Texts related to system behaviour / Label text
200040027 | Flexible Modbus | Texts related to system behaviour / Label text
200040028 | Fieldbus configuration | Texts related to system behaviour / Label text
200040029 | Fieldbus supervision | Texts related to system behaviour / Label text
200040030 | Restore configuration | Texts related to system behaviour / Label text
200040031 | Engine Interface J1939 DM2 log | Texts related to system behaviour / Label text
200040032 | Engine Interface Communication | Texts related to system behaviour / Label text
200040033 | Trending | Texts related to system behaviour / Label text
200040034 | IO status | Texts related to system behaviour / Label text
200040035 | Dashboard design | Texts related to system behaviour / Label text
200050000 | Value changed event | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050001 | Command event | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050002 | Master display changed | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050003 | Name | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050004 | IP address | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050005 | Backup created | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050006 | Restore started | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050007 | Backup restored | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050008 | Backup file deleted | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050009 | Controller selected as time master | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050010 | Controller no longer selected as time master | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050011 | Reset alarm counters | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050012 | J1939 DM1 alarm | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050013 | J1939 DM1 alarm clear requested | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200050014 | Counter changed event | Texts related to system behaviour / Event text (pop-ups, logs and status texts)
200070000 | -25 to 25 mA | Texts related to system behaviour / Label text
200070001 | 0 to 20 mA | Texts related to system behaviour / Label text
200070002 | 4 to 25 mA | Texts related to system behaviour / Label text
200070003 | 0 to 25 mA | Texts related to system behaviour / Label text
200070004 | -20 to 20 mA | Texts related to system behaviour / Label text
200070005 | 0 to 2500 ohm | Texts related to system behaviour / Label text
200070006 | Pt100 ohm | Texts related to system behaviour / Label text
200070007 | Pt1000 ohm | Texts related to system behaviour / Label text
200070008 | 0 to 10 V | Texts related to system behaviour / Label text
200070009 | -10 to 10 V | Texts related to system behaviour / Label text
200070010 | -5 to 5 V | Texts related to system behaviour / Label text
200070011 | 0 to 100 % | Texts related to system behaviour / Label text
200070012 | No unit | Texts related to system behaviour / Label text
200070013 | Dry contact | Texts related to system behaviour / Label text
200070014 | Thermocouple B | Texts related to system behaviour / Label text
200070015 | Thermocouple E | Texts related to system behaviour / Label text
200070016 | Thermocouple J | Texts related to system behaviour / Label text
200070017 | Thermocouple K | Texts related to system behaviour / Label text
200070018 | Thermocouple N | Texts related to system behaviour / Label text
200070019 | Thermocouple R | Texts related to system behaviour / Label text
200070020 | Thermocouple S | Texts related to system behaviour / Label text
200070021 | Thermocouple T | Texts related to system behaviour / Label text
200070022 | PWM | Texts related to system behaviour / Label text
200070023 | Pt100 ohm 2-wire | Texts related to system behaviour / Label text
200070024 | Pt100 ohm 3-wire | Texts related to system behaviour / Label text
200070025 | Pt1000 ohm 2-wire | Texts related to system behaviour / Label text
200070026 | Pt1000 ohm 3-wire | Texts related to system behaviour / Label text
200070027 | 0 to 4500 ohm 2-wire | Texts related to system behaviour / Label text
200070028 | 0 to 4500 ohm 3-wire | Texts related to system behaviour / Label text
200070030 | kPa to bar | Texts related to system behaviour / Label text
200070031 | kPa to mbar | Texts related to system behaviour / Label text
200070032 | Temperature | Texts related to system behaviour / Label text
200070033 | Percent | Texts related to system behaviour / Label text
200070034 | Ampere | Texts related to system behaviour / Label text
200070035 | RPM | Texts related to system behaviour / Label text
200070036 | Degrees Angle | Texts related to system behaviour / Label text
200070037 | Hour | Texts related to system behaviour / Label text
200070038 | MPa to bar | Texts related to system behaviour / Label text
200070039 | Flow | Texts related to system behaviour / Label text
200070040 | Voltage | Texts related to system behaviour / Label text
200070041 | Power | Texts related to system behaviour / Label text
200070042 | litre | Texts related to system behaviour / Label text
200070043 | Mass | Texts related to system behaviour / Label text
200070044 | Mass | Texts related to system behaviour / Label text
200070045 | Mass flow | Texts related to system behaviour / Label text
200070046 | Voltage | Texts related to system behaviour / Label text
200070047 | Ampere | Texts related to system behaviour / Label text
200070048 | AC RMS voltage | Texts related to system behaviour / Label text
200070049 | AC frequency | Texts related to system behaviour / Label text
200070050 | AC RMS current | Texts related to system behaviour / Label text
200070051 | Reactive power | Texts related to system behaviour / Label text
200070052 | PF | Texts related to system behaviour / Label text
200070053 | PF lagging | Texts related to system behaviour / Label text
200070054 | Active power | Texts related to system behaviour / Label text
200070055 | Apparent power | Texts related to system behaviour / Label text
200070056 | DVC Pt100 | Texts related to system behaviour / Label text
200070057 | 0 to 10000 ohm | Texts related to system behaviour / Label text
200080001 | Unknown | Texts related to system behaviour / Label text
200086001 | Generic J1939 | Texts related to system behaviour / Label text
200086002 | Volvo Penta EMS2 2.3 | Texts related to system behaviour / Label text
200086003 | Volvo Penta EMS2 2.4 | Texts related to system behaviour / Label text
200086004 | Detroit Diesel DDEC 3 | Texts related to system behaviour / Label text
200086005 | Detroit Diesel DDEC 4 | Texts related to system behaviour / Label text
200086006 | Caterpillar ADEM3 | Texts related to system behaviour / Label text
200086007 | Caterpillar A4 | Texts related to system behaviour / Label text
200086008 | Perkins ADEM 3 | Texts related to system behaviour / Label text
200086009 | Perkins A4 | Texts related to system behaviour / Label text
200086010 | Cummins CM 500 | Texts related to system behaviour / Label text
200086011 | Cummins CM 558 | Texts related to system behaviour / Label text
200086012 | Cummins CM 570 | Texts related to system behaviour / Label text
200086013 | Cummins CM 850 | Texts related to system behaviour / Label text
200086014 | Cummins CM 2150 | Texts related to system behaviour / Label text
200086015 | Cummins CM 2250 | Texts related to system behaviour / Label text
200086016 | Deutz EMR 2 | Texts related to system behaviour / Label text
200086017 | Deutz EMR 3 | Texts related to system behaviour / Label text
200086018 | Isuzu ECM | Texts related to system behaviour / Label text
200086019 | Iveco EDC7 (Bosch MS6.2) | Texts related to system behaviour / Label text
200086020 | Iveco NEF | Texts related to system behaviour / Label text
200086021 | Iveco CURSOR | Texts related to system behaviour / Label text
200086022 | Iveco VECTOR 8 | Texts related to system behaviour / Label text
200086023 | John Deere | Texts related to system behaviour / Label text
200086024 | Kohler KD62V12 | Texts related to system behaviour / Label text
200086025 | Badouin Wise15 | Texts related to system behaviour / Label text
200086029 | MTU J1939 Smart Connect | Texts related to system behaviour / Label text
200086030 | MTU J1939 ECU8 | Texts related to system behaviour / Label text
200086031 | MTU J1939 ECU9 | Texts related to system behaviour / Label text
200086036 | Power Solutions (PSI) | Texts related to system behaviour / Label text
200086037 | Scania EMS | Texts related to system behaviour / Label text
200086038 | Scania EMS2 S6 | Texts related to system behaviour / Label text
200086039 | Scania EMS2 S8 | Texts related to system behaviour / Label text
200086040 | Volvo Penta EDC4 | Texts related to system behaviour / Label text
200086041 | Volvo Penta EMS | Texts related to system behaviour / Label text
200086042 | Volvo Penta EDC3 | Texts related to system behaviour / Label text
200086043 | John Deere Stage 5 | Texts related to system behaviour / Label text
200086044 | Detroit Diesel DDEC generic | Texts related to system behaviour / Label text
200086045 | Perkins generic | Texts related to system behaviour / Label text
200086046 | Cummins generic | Texts related to system behaviour / Label text
200086047 | Deutz EMR generic | Texts related to system behaviour / Label text
200086048 | Volvo Penta generic | Texts related to system behaviour / Label text
200086049 | MTU J1939 CPC4 | Texts related to system behaviour / Label text
200086050 | Badouin Gas | Texts related to system behaviour / Label text
200086051 | Badouin Wise10B | Texts related to system behaviour / Label text
200086052 | FPT Stage V | Texts related to system behaviour / Label text
200086053 | Iveco Stage V | Texts related to system behaviour / Label text
200086054 | Perkins StV 1200 | Texts related to system behaviour / Label text
200086055 | Perkins StV 400 | Texts related to system behaviour / Label text
200086056 | Weichai Wise10B | Texts related to system behaviour / Label text
200086057 | Weichai Wise15 | Texts related to system behaviour / Label text
200086058 | MAN EDC17 | Texts related to system behaviour / Label text
200086059 | MAN EMC Step 2.0 | Texts related to system behaviour / Label text
200086060 | Doosan G2 EDC17 | Texts related to system behaviour / Label text
200086061 | FPT EDC17CV41 | Texts related to system behaviour / Label text
200086062 | Hatz EDC17 | Texts related to system behaviour / Label text
200086063 | MAN generic | Texts related to system behaviour / Label text
200086064 | Perkins ADEM4 | Texts related to system behaviour / Label text
200086065 | Steyr EDC17 | Texts related to system behaviour / Label text
200086066 | Yuchai YC-BCR | Texts related to system behaviour / Label text
200086067 | Yuchai YC-ECU | Texts related to system behaviour / Label text
200086068 | Doosan MD1 | Texts related to system behaviour / Label text
200086069 | YANMAR EDC17 | Texts related to system behaviour / Label text
200086070 | FMS | Texts related to system behaviour / Label text
200086071 | Yuchai United Diesel | Texts related to system behaviour / Label text
200086072 | Yuchai United Gas | Texts related to system behaviour / Label text
200086073 | Weichai Diesel | Texts related to system behaviour / Label text
200086074 | Weichai Gas | Texts related to system behaviour / Label text
200086075 | MAN EMC Step 2.5 | Texts related to system behaviour / Label text
200086076 | Iveco generic | Texts related to system behaviour / Label text
200086077 | Perkins EDC17C49 | Texts related to system behaviour / Label text
200086078 | Caterpillar ADEM 4 | Texts related to system behaviour / Label text
200086079 | Caterpillar generic | Texts related to system behaviour / Label text
200086080 | Deutz EMR 4 | Texts related to system behaviour / Label text
200086081 | Deutz EMR 5 | Texts related to system behaviour / Label text
200086082 | Engine Protocol 82 | Texts related to system behaviour / Label text
200087000 | DEIF DVC 550 | Texts related to system behaviour / Label text
200087001 | DEIF DVC 350 | Texts related to system behaviour / Label text
200087002 | Leroy Somer D550 | Texts related to system behaviour / Label text
200087003 | Leroy Somer D350 | Texts related to system behaviour / Label text
200100000 | Application | Texts related to system behaviour / Label text
200100001 | Bootloader | Texts related to system behaviour / Label text
200100002 | Download | Texts related to system behaviour / Label text
200100003 | Operating system | Texts related to system behaviour / Label text
200100004 | Framework | Texts related to system behaviour / Label text
200100005 | Software | Texts related to system behaviour / Label text
200100006 | Hardware | Texts related to system behaviour / Label text
200100007 | Interface | Texts related to system behaviour / Label text
200100009 | BSP | Texts related to system behaviour / Label text
200110000 | YYYY-MM-DD | Texts related to system behaviour / Label text
200110001 | YY-MM-DD | Texts related to system behaviour / Label text
200110002 | DD-MM-YYYY | Texts related to system behaviour / Label text
200110003 | DD-MM-YY | Texts related to system behaviour / Label text
200110004 | MM-DD-YYYY | Texts related to system behaviour / Label text
200110005 | MM-DD-YY | Texts related to system behaviour / Label text
200120000 | Standard node (sub-ring) | Texts related to system behaviour / Label text
200120001 | Interconnection node (major ring) | Texts related to system behaviour / Label text
200120010 | Automatic | Texts related to system behaviour / Label text
200120011 | Standard (sub-ring) | Texts related to system behaviour / Label text
200120012 | Interconnection (major ring) | Texts related to system behaviour / Label text
200120013 | Display unit | Texts related to system behaviour / Label text
200120014 | External network/PICUS | Texts related to system behaviour / Label text
200120015 | Disabled | Texts related to system behaviour / Label text
200120020 | Port 1 | Texts related to system behaviour / Label text
200120021 | Port 2 | Texts related to system behaviour / Label text
200120022 | Port 3 | Texts related to system behaviour / Label text
200120023 | Port 4 | Texts related to system behaviour / Label text
200120024 | Port 5 | Texts related to system behaviour / Label text
200220000 | Redundancy connection | Texts related to system behaviour / Label text
200220001 | Single connection | Texts related to system behaviour / Label text
200220002 | Split connection | Texts related to system behaviour / Label text
200220003 | Bus connection | Texts related to system behaviour / Label text
201000000 | Custom input curve 1 | Texts related to scaling of values on graphs etc. / Label text
201000001 | Custom input curve 2 | Texts related to scaling of values on graphs etc. / Label text
201000002 | Custom input curve 3 | Texts related to scaling of values on graphs etc. / Label text
201000003 | Custom input curve 4 | Texts related to scaling of values on graphs etc. / Label text
201000004 | Custom input curve 5 | Texts related to scaling of values on graphs etc. / Label text
201000005 | Custom input curve 6 | Texts related to scaling of values on graphs etc. / Label text
201000006 | Custom input curve 7 | Texts related to scaling of values on graphs etc. / Label text
201000007 | Custom input curve 8 | Texts related to scaling of values on graphs etc. / Label text
201000008 | Custom input curve 9 | Texts related to scaling of values on graphs etc. / Label text
201000009 | Custom input curve 10 | Texts related to scaling of values on graphs etc. / Label text
201000010 | Custom input curve 11 | Texts related to scaling of values on graphs etc. / Label text
201000011 | Custom input curve 12 | Texts related to scaling of values on graphs etc. / Label text
201000012 | Custom input curve 13 | Texts related to scaling of values on graphs etc. / Label text
201000013 | Custom input curve 14 | Texts related to scaling of values on graphs etc. / Label text
201000014 | Custom input curve 15 | Texts related to scaling of values on graphs etc. / Label text
201000015 | Custom input curve 16 | Texts related to scaling of values on graphs etc. / Label text
201000016 | Custom input curve 17 | Texts related to scaling of values on graphs etc. / Label text
201000017 | Custom input curve 18 | Texts related to scaling of values on graphs etc. / Label text
201000018 | Custom input curve 19 | Texts related to scaling of values on graphs etc. / Label text
201000019 | Custom input curve 20 | Texts related to scaling of values on graphs etc. / Label text
201010000 | Custom output curve 1 | Texts related to scaling of values on graphs etc. / Label text
201010001 | Custom output curve 2 | Texts related to scaling of values on graphs etc. / Label text
201010002 | Custom output curve 3 | Texts related to scaling of values on graphs etc. / Label text
201010003 | Custom output curve 4 | Texts related to scaling of values on graphs etc. / Label text
201010004 | Custom output curve 5 | Texts related to scaling of values on graphs etc. / Label text
201010005 | Custom output curve 6 | Texts related to scaling of values on graphs etc. / Label text
201010006 | Custom output curve 7 | Texts related to scaling of values on graphs etc. / Label text
201010007 | Custom output curve 8 | Texts related to scaling of values on graphs etc. / Label text
201010008 | Custom output curve 9 | Texts related to scaling of values on graphs etc. / Label text
201010009 | Custom output curve 10 | Texts related to scaling of values on graphs etc. / Label text
201010010 | Custom output curve 11 | Texts related to scaling of values on graphs etc. / Label text
201010011 | Custom output curve 12 | Texts related to scaling of values on graphs etc. / Label text
201010012 | Custom output curve 13 | Texts related to scaling of values on graphs etc. / Label text
201010013 | Custom output curve 14 | Texts related to scaling of values on graphs etc. / Label text
201010014 | Custom output curve 15 | Texts related to scaling of values on graphs etc. / Label text
201010015 | Custom output curve 16 | Texts related to scaling of values on graphs etc. / Label text
201010016 | Custom output curve 17 | Texts related to scaling of values on graphs etc. / Label text
201010017 | Custom output curve 18 | Texts related to scaling of values on graphs etc. / Label text
201010018 | Custom output curve 19 | Texts related to scaling of values on graphs etc. / Label text
201010019 | Custom output curve 20 | Texts related to scaling of values on graphs etc. / Label text
201020015 | (4 to 20mA) to (0 to 100%) | Texts related to scaling of values on graphs etc. / Label text
201020016 | Thermocouple type E | Texts related to scaling of values on graphs etc. / Label text
201020017 | Thermocouple type J | Texts related to scaling of values on graphs etc. / Label text
201020018 | Thermocouple type K | Texts related to scaling of values on graphs etc. / Label text
201020019 | Thermocouple type N | Texts related to scaling of values on graphs etc. / Label text
201020020 | Thermocouple type R | Texts related to scaling of values on graphs etc. / Label text
201020021 | Thermocouple type S | Texts related to scaling of values on graphs etc. / Label text
201020022 | Thermocouple type T | Texts related to scaling of values on graphs etc. / Label text
201020025 | kPa to bar (0 - 1000 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020027 | kPa to bar (0 - 500 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020029 | kPa to bar (0 - 125 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020031 | kPa to bar (0 - 12.5 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020033 | kPa to bar (-250 - 251.99 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020035 | kPa to bar (0 - 1250 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020037 | kPa to bar (0 - 2000 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020039 | kPa to bar (0 - 6425.5 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020041 | kPa to bar (0 - 8031.875 kPa) | Texts related to scaling of values on graphs etc. / Label text
201020043 | Temperature | Texts related to scaling of values on graphs etc. / Label text
201020044 | Temperature | Texts related to scaling of values on graphs etc. / Label text
201020045 | Percent | Texts related to scaling of values on graphs etc. / Label text
201020046 | Percent | Texts related to scaling of values on graphs etc. / Label text
201020047 | Percent | Texts related to scaling of values on graphs etc. / Label text
201020048 | Percent | Texts related to scaling of values on graphs etc. / Label text
201020049 | Percent | Texts related to scaling of values on graphs etc. / Label text
201020050 | Percent | Texts related to scaling of values on graphs etc. / Label text
201020051 | Ampere | Texts related to scaling of values on graphs etc. / Label text
201020052 | RPM | Texts related to scaling of values on graphs etc. / Label text
201020053 | RPM | Texts related to scaling of values on graphs etc. / Label text
201020054 | Degrees | Texts related to scaling of values on graphs etc. / Label text
201020055 | Hours | Texts related to scaling of values on graphs etc. / Label text
201020056 | Hours | Texts related to scaling of values on graphs etc. / Label text
201020057 | MPa to bar (0 - 250.996 MPa) | Texts related to scaling of values on graphs etc. / Label text
201020058 | bit states | Texts related to scaling of values on graphs etc. / Label text
201020059 | bit states | Texts related to scaling of values on graphs etc. / Label text
201020060 | bit states | Texts related to scaling of values on graphs etc. / Label text
201020061 | bit states | Texts related to scaling of values on graphs etc. / Label text
201020062 | L/h (0 - 3212.75 L/h) | Texts related to scaling of values on graphs etc. / Label text
201020063 | Voltage | Texts related to scaling of values on graphs etc. / Label text
201020064 | Power | Texts related to scaling of values on graphs etc. / Label text
201020065 | Litre | Texts related to scaling of values on graphs etc. / Label text
201020066 | Mass | Texts related to scaling of values on graphs etc. / Label text
201020067 | bit states | Texts related to scaling of values on graphs etc. / Label text
201020068 | Mass | Texts related to scaling of values on graphs etc. / Label text
201020069 | Mass flow | Texts related to scaling of values on graphs etc. / Label text
201020070 | Mass | Texts related to scaling of values on graphs etc. / Label text
201020071 | AC voltage | Texts related to scaling of values on graphs etc. / Label text
201020072 | Ampere | Texts related to scaling of values on graphs etc. / Label text
201020073 | AC voltage | Texts related to scaling of values on graphs etc. / Label text
201020074 | Frequency | Texts related to scaling of values on graphs etc. / Label text
201020075 | Ampere | Texts related to scaling of values on graphs etc. / Label text
201020076 | Reactive power | Texts related to scaling of values on graphs etc. / Label text
201020077 | Power factor | Texts related to scaling of values on graphs etc. / Label text
201020078 | Watts | Texts related to scaling of values on graphs etc. / Label text
201020079 | Apparent power | Texts related to scaling of values on graphs etc. / Label text
201020080 | Temperature | Texts related to scaling of values on graphs etc. / Label text
201030000 | (0 to 100 %) to (0 to 10 V) | Texts related to scaling of values on graphs etc. / Label text
201030001 | (-100 to 100 %) to (0 to 10 V) | Texts related to scaling of values on graphs etc. / Label text
201030002 | (0 to 100 %) to (-10 to 10 V) | Texts related to scaling of values on graphs etc. / Label text
201030003 | (-100 to 100 %) to (-10 to 10 V) | Texts related to scaling of values on graphs etc. / Label text
201030004 | (0 to 100 %) to (0 to 20 mA) | Texts related to scaling of values on graphs etc. / Label text
201030005 | (-100 to 100 %) to (0 to 20 mA) | Texts related to scaling of values on graphs etc. / Label text
201030006 | (0 to 100 %) to (4 to 20 mA) | Texts related to scaling of values on graphs etc. / Label text
201030007 | (-100 to 100 %) to (4 to 20 mA) | Texts related to scaling of values on graphs etc. / Label text
201030008 | (0 to 100 %) to (-25 to 25 mA) | Texts related to scaling of values on graphs etc. / Label text
201030009 | (-100 to 100 %) to (-25 to 25 mA) | Texts related to scaling of values on graphs etc. / Label text
201030010 | (0 to 100 %) to (0 to 100 %) | Texts related to scaling of values on graphs etc. / Label text
201030011 | (-100 to 100 %) to (0 to 100 %) | Texts related to scaling of values on graphs etc. / Label text
202000001 | Digital input 1 | Texts related to naming of system interfaces and ports / Label text
202000002 | Digital input 2 | Texts related to naming of system interfaces and ports / Label text
202000003 | Digital input 3 | Texts related to naming of system interfaces and ports / Label text
202000004 | Digital input 4 | Texts related to naming of system interfaces and ports / Label text
202000005 | Digital input 5 | Texts related to naming of system interfaces and ports / Label text
202000006 | Digital input 6 | Texts related to naming of system interfaces and ports / Label text
202000007 | Digital input 7 | Texts related to naming of system interfaces and ports / Label text
202000008 | Digital input 8 | Texts related to naming of system interfaces and ports / Label text
202000009 | Digital input 9 | Texts related to naming of system interfaces and ports / Label text
202000010 | Digital input 10 | Texts related to naming of system interfaces and ports / Label text
202000011 | Digital input 11 | Texts related to naming of system interfaces and ports / Label text
202000012 | Digital input 12 | Texts related to naming of system interfaces and ports / Label text
202000013 | Digital input 13 | Texts related to naming of system interfaces and ports / Label text
202000014 | Digital input 14 | Texts related to naming of system interfaces and ports / Label text
202000015 | Digital input 15 | Texts related to naming of system interfaces and ports / Label text
202000016 | Digital input 16 | Texts related to naming of system interfaces and ports / Label text
202000501 | Digital output 1 | Texts related to naming of system interfaces and ports / Label text
202000502 | Digital output 2 | Texts related to naming of system interfaces and ports / Label text
202000503 | Digital output 3 | Texts related to naming of system interfaces and ports / Label text
202000504 | Digital output 4 | Texts related to naming of system interfaces and ports / Label text
202000505 | Digital output 5 | Texts related to naming of system interfaces and ports / Label text
202000506 | Digital output 6 | Texts related to naming of system interfaces and ports / Label text
202000507 | Digital output 7 | Texts related to naming of system interfaces and ports / Label text
202000508 | Digital output 8 | Texts related to naming of system interfaces and ports / Label text
202000509 | Digital output 9 | Texts related to naming of system interfaces and ports / Label text
202000510 | Digital output 10 | Texts related to naming of system interfaces and ports / Label text
202000511 | Digital output 11 | Texts related to naming of system interfaces and ports / Label text
202000512 | Digital output 12 | Texts related to naming of system interfaces and ports / Label text
202000513 | Digital output 13 | Texts related to naming of system interfaces and ports / Label text
202000514 | Digital output 14 | Texts related to naming of system interfaces and ports / Label text
202000515 | Digital output 15 | Texts related to naming of system interfaces and ports / Label text
202000516 | Digital output 16 | Texts related to naming of system interfaces and ports / Label text
202001001 | Analogue input 1 | Texts related to naming of system interfaces and ports / Label text
202001002 | Analogue input 2 | Texts related to naming of system interfaces and ports / Label text
202001003 | Analogue input 3 | Texts related to naming of system interfaces and ports / Label text
202001004 | Analogue input 4 | Texts related to naming of system interfaces and ports / Label text
202001005 | Analogue input 5 | Texts related to naming of system interfaces and ports / Label text
202001006 | Analogue input 6 | Texts related to naming of system interfaces and ports / Label text
202001007 | Analogue input 7 | Texts related to naming of system interfaces and ports / Label text
202001008 | Analogue input 8 | Texts related to naming of system interfaces and ports / Label text
202001009 | Analogue input 9 | Texts related to naming of system interfaces and ports / Label text
202001010 | Analogue input 10 | Texts related to naming of system interfaces and ports / Label text
202001501 | Analogue output 1 | Texts related to naming of system interfaces and ports / Label text
202001502 | Analogue output 2 | Texts related to naming of system interfaces and ports / Label text
202001503 | Analogue output 3 | Texts related to naming of system interfaces and ports / Label text
202001504 | Analogue output 4 | Texts related to naming of system interfaces and ports / Label text
202002000 | PWM output | Texts related to naming of system interfaces and ports / Label text
202002500 | MPU/W input | Texts related to naming of system interfaces and ports / Label text
202003000 | Load sharing | Texts related to naming of system interfaces and ports / Label text
202003001 | Parameter list | Texts related to naming of system interfaces and ports / Label text
202003002 | AC inputs | Texts related to naming of system interfaces and ports / Label text
202003500 | Digital input/output 1 | Texts related to naming of system interfaces and ports / Label text
202003501 | Digital input/output 2 | Texts related to naming of system interfaces and ports / Label text
202003502 | Digital input/output 3 | Texts related to naming of system interfaces and ports / Label text
202003503 | Digital input/output 4 | Texts related to naming of system interfaces and ports / Label text
202003504 | Digital input/output 5 | Texts related to naming of system interfaces and ports / Label text
202003505 | Digital input/output 6 | Texts related to naming of system interfaces and ports / Label text
202003506 | Digital input/output 7 | Texts related to naming of system interfaces and ports / Label text
202003507 | Digital input/output 8 | Texts related to naming of system interfaces and ports / Label text
202003508 | Digital input/output 9 | Texts related to naming of system interfaces and ports / Label text
202003509 | Digital input/output 10 | Texts related to naming of system interfaces and ports / Label text
202003510 | Digital input/output 11 | Texts related to naming of system interfaces and ports / Label text
202003511 | Digital input/output 12 | Texts related to naming of system interfaces and ports / Label text
202003512 | Digital input/output 13 | Texts related to naming of system interfaces and ports / Label text
202003513 | Digital input/output 14 | Texts related to naming of system interfaces and ports / Label text
202003514 | Digital input/output 15 | Texts related to naming of system interfaces and ports / Label text
202003515 | Digital input/output 16 | Texts related to naming of system interfaces and ports / Label text
202003516 | Digital input/output 17 | Texts related to naming of system interfaces and ports / Label text
202003517 | Digital input/output 18 | Texts related to naming of system interfaces and ports / Label text
202003518 | Digital input/output 19 | Texts related to naming of system interfaces and ports / Label text
202003519 | Digital input/output 20 | Texts related to naming of system interfaces and ports / Label text
203004000 | Functions | Texts related to CustomLogic feature / Menu text (menu hierachy and labels)
203005000 | Parameters | Texts related to CustomLogic feature / Menu text (menu hierachy and labels)
203006000 | Alarms | Texts related to CustomLogic feature / Menu text (menu hierachy and labels)
203007000 | ICC | Texts related to CustomLogic feature / Menu text (menu hierachy and labels)
203007001 | Inter-controller communication | Texts related to CustomLogic feature / Menu text (menu hierachy and labels)
203008000 | I/O | Texts related to CustomLogic feature / Menu text (menu hierachy and labels)
203009000 | Counters | Texts related to CustomLogic feature / Menu text (menu hierachy and labels)
203010000 | Custom digital input | Texts related to CustomLogic feature / Assignable function (input/output config menus, Modbus)
203010001 | Custom digital output | Texts related to CustomLogic feature / Assignable function (input/output config menus, Modbus)
203010002 | Custom analogue input | Texts related to CustomLogic feature / Assignable function (input/output config menus, Modbus)
203010003 | Custom analogue output | Texts related to CustomLogic feature / Assignable function (input/output config menus, Modbus)
203100000 | Custom digital input | Texts related to the CODESYS Development System / Assignable function (input/output config menus, Modbus)
203101000 | Custom digital output | Texts related to the CODESYS Development System / Assignable function (input/output config menus, Modbus)
203102000 | Custom analogue input | Texts related to the CODESYS Development System / Assignable function (input/output config menus, Modbus)
203103000 | Custom analogue output | Texts related to the CODESYS Development System / Assignable function (input/output config menus, Modbus)
203108000 | CODESYS vta %s | Texts related to the CODESYS Development System / Label text
203120000 | CODESYS Modbus Coil | Texts related to the CODESYS Development System / Label text
203121000 | CODESYS Modbus Input | Texts related to the CODESYS Development System / Label text
203122000 | CODESYS Modbus Holding | Texts related to the CODESYS Development System / Label text
203123000 | CODESYS Modbus Register | Texts related to the CODESYS Development System / Label text
203200000 | success | Texts related to backup/restore of system setup and application / Status text (info lines)
203200001 | Unexpected error | Texts related to backup/restore of system setup and application / Status text (info lines)
203200002 | Backup not present in backup location | Texts related to backup/restore of system setup and application / Status text (info lines)
203200003 | Backup failed: Maximum number of controller backups reached | Texts related to backup/restore of system setup and application / Status text (info lines)
203200004 | Backup deleted | Texts related to backup/restore of system setup and application / Status text (info lines)
203200005 | Backup failed: System error | Texts related to backup/restore of system setup and application / Status text (info lines)
203200006 | Backup failed: Could not copy file | Texts related to backup/restore of system setup and application / Status text (info lines)
203200007 | Backup failed: Could not create .tar-file | Texts related to backup/restore of system setup and application / Status text (info lines)
203200008 | Backup failed: Could not create .dupdate-file | Texts related to backup/restore of system setup and application / Status text (info lines)
203200009 | Backup failed: Could not create .backup-file | Texts related to backup/restore of system setup and application / Status text (info lines)
203200010 | Backup failed: Not enough space on selected location | Texts related to backup/restore of system setup and application / Status text (info lines)
203200011 | Backup could not be deleted | Texts related to backup/restore of system setup and application / Status text (info lines)
203200012 | Save to controller | Texts related to backup/restore of system setup and application / Status text (info lines)
203200013 | Save to SD card | Texts related to backup/restore of system setup and application / Status text (info lines)
203200014 | Backup created | Texts related to backup/restore of system setup and application / Status text (info lines)
203200015 | SD card failure | Texts related to backup/restore of system setup and application / Status text (info lines)
203200016 | Backup failed: Backup in progress | Texts related to backup/restore of system setup and application / Status text (info lines)
203200017 | Not used | Texts related to backup/restore of system setup and application / Status text (info lines)
203200018 | Backup creation started | Texts related to backup/restore of system setup and application / Status text (info lines)
203200019 | Controller | Texts related to backup/restore of system setup and application / Status text (info lines)
203200020 | SD card | Texts related to backup/restore of system setup and application / Status text (info lines)
203300000 | Restore failed | Texts related to backup/restore of system setup and application / Status text (info lines)
203300001 | Restore failed: Controller not ready for commissioning | Texts related to backup/restore of system setup and application / Status text (info lines)
203300002 | Restore failed: Backup made from different product type | Texts related to backup/restore of system setup and application / Status text (info lines)
203300003 | Restore failed: Controller software version does not support the backup files | Texts related to backup/restore of system setup and application / Status text (info lines)
203300004 | Restore failed: Backup made from controller with different hardware | Texts related to backup/restore of system setup and application / Status text (info lines)
203300005 | Restore failed: Backup made from different controller type | Texts related to backup/restore of system setup and application / Status text (info lines)
203300006 | Restore failed: Backup made from different controller configuration | Texts related to backup/restore of system setup and application / Status text (info lines)
203300007 | Restore failed: Restore process interrupted | Texts related to backup/restore of system setup and application / Status text (info lines)
203300008 | Restore IP address (IPv4) and controller ID | Texts related to backup/restore of system setup and application / Status text (info lines)
203300009 | Restore counters | Texts related to backup/restore of system setup and application / Status text (info lines)
203300010 | Restore started | Texts related to backup/restore of system setup and application / Status text (info lines)
203300011 | Restore failed: Restore in progress | Texts related to backup/restore of system setup and application / Status text (info lines)
203300012 | Restore application data | Texts related to backup/restore of system setup and application / Status text (info lines)
203300013 | Restore CODESYS application | Texts related to backup/restore of system setup and application / Status text (info lines)
203300014 | Restore IP address (IPv4), controller ID and port configuration | Texts related to backup/restore of system setup and application / Status text (info lines)
203400000 | Controller software running | Texts related to indication of system state / Status text (info lines)
203400001 | Controller software not running | Texts related to indication of system state / Status text (info lines)
203400002 | Controller software not running: Debug lock | Texts related to indication of system state / Status text (info lines)
203400003 | Controller starting | Texts related to indication of system state / Status text (info lines)
203400004 | Restoring data | Texts related to indication of system state / Status text (info lines)
203400005 | Firmware update started | Texts related to indication of system state / Status text (info lines)
203400006 | Updating hardware modules. Do not remove power. | Texts related to indication of system state / Status text (info lines)
203400007 | Installing controller software | Texts related to indication of system state / Status text (info lines)
203400008 | Firmware update failed | Texts related to indication of system state / Status text (info lines)
203500000 | Commands | Texts related to flexible Modbus / Modbus table text
203500001 | Configuration | Texts related to flexible Modbus / Modbus table text
203500002 | Information | Texts related to flexible Modbus / Modbus table text
203500003 | Remaining | Texts related to flexible Modbus / Modbus table text
203500004 | Elasped | Texts related to flexible Modbus / Modbus table text
203500005 | Running | Texts related to flexible Modbus / Modbus table text
203500006 | Out | Texts related to flexible Modbus / Modbus table text
203500007 | Priorities | Texts related to flexible Modbus / Modbus table text
203500008 | Texts | Texts related to flexible Modbus / Modbus table text
203500009 | Activate new priorities | Texts related to flexible Modbus / Modbus table text
203500010 | Flags | Texts related to flexible Modbus / Modbus table text
203500011 | Actual priorities | Texts related to flexible Modbus / Modbus table text
203500012 | Configure priorities | Texts related to flexible Modbus / Modbus table text
203500013 | Custom alarms | Texts related to flexible Modbus / Modbus table text
203500014 | Fieldbus | Texts related to flexible Modbus / Modbus table text
203600000 | Compensation 1 | Texts related to cold junction compensation feature / Assignable function (input/output config menus, Modbus)
203600001 | Compensation 2 | Texts related to cold junction compensation feature / Assignable function (input/output config menus, Modbus)
203600002 | Compensation 3 | Texts related to cold junction compensation feature / Assignable function (input/output config menus, Modbus)
203600003 | Compensation 4 | Texts related to cold junction compensation feature / Assignable function (input/output config menus, Modbus)
203600004 | Compensation 5 | Texts related to cold junction compensation feature / Assignable function (input/output config menus, Modbus)
203600005 | Compensation 6 | Texts related to cold junction compensation feature / Assignable function (input/output config menus, Modbus)
203600006 | Compensation 7 | Texts related to cold junction compensation feature / Assignable function (input/output config menus, Modbus)
203600007 | Compensation 8 | Texts related to cold junction compensation feature / Assignable function (input/output config menus, Modbus)
203601000 | Thermocouple cold junction | Texts related to cold junction compensation feature / Label text
203601001 | Cold junction | Texts related to cold junction compensation feature / Label text
203601002 | Internal compensation | Texts related to cold junction compensation feature / Label text
203601003 | No compensation | Texts related to cold junction compensation feature / Label text
203700000 | Monday | Texts regarding engineering units / Label text
203700001 | Tuesday | Texts regarding engineering units / Label text
203700002 | Wednesday | Texts regarding engineering units / Label text
203700003 | Thursday | Texts regarding engineering units / Label text
203700004 | Friday | Texts regarding engineering units / Label text
203700005 | Saturday | Texts regarding engineering units / Label text
203700006 | Sunday | Texts regarding engineering units / Label text
301000200 | Parameters | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010000 | Ground | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010001 | 12 or 24 V DC | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010002 | Relay output | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010003 | Relay output (with wire break detection) | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010004 | Transistor output | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010005 | Digital input | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010006 | Analogue current/voltage output | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010007 | Analogue current/resistance input | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010008 | Analogue current/voltage input | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010009 | Analogue input | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010010 | PWM output | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010011 | W input | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010012 | MPU input | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010013 | Load sharing | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010014 | Internal communication (RJ45) | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010015 | Voltage | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010016 | Current | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010017 | Ethernet (RJ45) | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010018 | CAN bus connection | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010019 | SD card | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010020 | Analogue current/voltage/PWM output | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010021 | Analogue voltage/current/resistance input | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010022 | Digital input/output | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)
301010023 | Analogue input/output | Texts related to naming of system interfaces and ports / Terminal hardware property (labels, list)